# COMMISSION ACTION MATRIX plumbing, electrical, mechanical and energy (peme) CODE ADVISORY COMMITTEE

## 2022 california plumbing code, TITLE 24, PART 5, AGENCY: The office of statewide health planning and development, OSHPD 06/22

### LEGEND:

**CAC Actions:** Approve, Disapprove, Approve as Amended, Further Study Required

**Agency Responses:** Accept, Disagree, Withdraw

**CBSC Actions:** Approve, Disapprove, Approve as Amended, Further Study Required

**Matrix Paper Color** (for commission action only): GREEN = uncontested items, YELLOW = challenged items, SALMON = withdrawn, no action required

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic and ellipsis.

* Model Code language appears upright
* Existing California amendments appear in *italic*
* Amended model code or new California amendments appear *underlined & italic*
* Repealed model code language appears ~~upright and in strikeout~~
* Repealed California amendments appear in *~~italic and strikeout~~*
* Ellipses (...) indicate existing text remains unchanged

### Chapter 2, definitions Section 210.0

OSHPD proposes to amend existing section listed below.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item Number 1** | **Code Section** | **CAC Action** | **Agency Response** | **Public Comments** | **Annotations** | **CBSC Action** |
| OSHPD-06/22-1 | *Handwashing Fixture* | **Approve** | **Accept** |  | Propose to add a tolerance to the existing California amendment to align with currently available products. |  |

### Chapter 3, general regulations, Section 310.9 prohibited fittings and practices

OSHPD proposes to amend existing section listed below.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item Number 2** | **Code Section** | **CAC Action** | **Agency Response** | **Public Comments** | **Annotations** | **CBSC Action** |
| OSHPD-06/22-2 | *310.9* | **Approve** | **Accept** |  | Propose to revise existing California amendment by adding compounding ante and buffer rooms to the text. |  |

### Chapter 3, general regulations, Section 321.0 essential plumbing provisions

OSHPD proposes to amend existing section listed below.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item Number 3** | **Code Section** | **CAC Action** | **Agency Response** | **Public Comments** | **Annotations** | **CBSC Action** |
| OSHPD-06/22-3 | *321.0* | **Approve** | **Accept** |  | Propose to revise existing California amendment by adding essential power for domestic hot water temp alarm. |  |

### Chapter 4, plumbing fixture and fixture fittings Section 422.1 fixture count

OSHPD proposes to amend existing sections listed below.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item Number 4** | **Code Section** | **CAC Action** | **Agency Response** | **Public Comments** | **Annotations** | **CBSC Action** |
| OSHPD-06/22-4-1 | *422.1* | **Approve** | **Accept** |  | Propose to repeal “Table 4-3” from the text; Table 4-2 provides fixture counts based on healthcare facilities. Also add new reference for Table 4-2 for OSHPD 1-5) for the minimum number plumbing fixtures. |  |
| OSHPD-06/22-4-2 | *422.1.3* | **Approve** | **Accept** |  | Propose to remove redundant language and add to 422.1. |  |

### Chapter 4, Plumbing fixtures and fixture fittings, table 4-2 minimum plumbing facilities

OSHPD proposes to amend Table as listed below.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item Number 5** | **Code Section** | **CAC Action** | **Agency Response** | **Public Comments** | **Annotations** | **CBSC Action** |
| OSHPD-06/22-5 | *Table 4-2* | **Approve** | **Disagree** |  | Propose to revise and update Table 4-2, amend existing, and add new footnotes.  **OSHPD**: Added two additional rooms to the Table to align with the CBC. |  |

### Chapter 6, water supply and distribution, Section 605.9.1 fittings

OSHPD proposes to amend existing section listed below.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item Number 6** | **Code Section** | **CAC Action** | **Agency Response** | **Public Comments** | **Annotations** | **CBSC Action** |
| OSHPD-06/22-6 | 609.9.1 | **Approve** | **Accept** |  | Propose to revise existing amendment, to repeal identifying year on the NSF standard. |  |

### Chapter 6, water supply and distribution, Section 613.0 domestic hot-water distribution systems for health facilities and clinics

OSHPD proposes to amend existing section listed below.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item Number 7** | **Code Section** | **CAC Action** | **Agency Response** | **Public Comments** | **Annotations** | **CBSC Action** |
| OSHPD-06/22-7-1 | *613.0* | **Approve** | **Accept** |  | Propose to remove OSHPD 1R designation. |  |
| OSHPD-06/22-7-2 | *613.2*  *Exception* | **Further Study** | **Accept** |  | Propose to add new exception for primary care clinics to existing California amendment for redundant hot water equipment.  **CAC**: 9 Pt Criteria 6. Consider changing “may” which is permissive, shall is required. Further Study to clarify the wording for primary care clinics to ensure application. OSHPD recommended changing the *Exception* approval from OSHPD to the Authority Having Jurisdiction (AHJ).  **OSHPD**: ***Exception*** has been changed from “may” to “shall”. Upon further study, OSHPD added that the use also include non-specialty clinics. |  |

### Chapter 6, water supply and distribution, Section 614.1 dialysis water-distribution systems

OSHPD proposes to amend existing section listed below.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item Number 8** | **Code Section** | **CAC Action** | **Agency Response** | **Public Comments** | **Annotations** | **CBSC Action** |
| OSHPD-06/22-8 | *614.1* | **Approve** | **Accept** |  | Propose to remove OSHPD 1R designation and further amend to allow dialysis piping to match current referenced standard. |  |

### Chapter 6, water supply and distribution, Section 615.4.1 emergency water supply

OSHPD proposes to amend existing section listed below.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item Number 9** | **Code Section** | **CAC Action** | **Agency Response** | **Public Comments** | **Annotations** | **CBSC Action** |
| OSHPD-06/22-9 | *615.4.1* | **Approve** | **Accept** |  | Propose to update referenced section number from CBC. |  |

### Chapter 7, Sanitary drainage, Section 727.1 emergency sanitary drainage

OSHPD proposes to amend existing section listed below.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item Number 10** | **Code Section** | **CAC Action** | **Agency Response** | **Public Comments** | **Annotations** | **CBSC Action** |
| OSHPD-06/22-10 | *727.1* | **Approve** | **Accept** |  | Propose to update referenced section number from CBC. |  |