# COMMISSION ACTION MATRIX 
GREEN Building – PLUMBING, ELECTRICAL, MECHANICAL & ENERGY AD-HOC (GREEN/PEME) CODE ADVISORY COMMITTEE
February 11-12, 2026

## 2025 California electrical code, TITLE 24, PART 3
AGENCY: office of statewide health planning and development, oshpd 04/25

### LEGEND:

CAC Actions: Approve, Disapprove, Approve as Amended, Further Study Required

Agency Responses: Accept, Disagree, Withdraw

CBSC Actions: Approve, Disapprove, Approve as Amended, Further Study Required

Matrix Paper Color (for commission action only): GREEN = uncontested items, YELLOW = challenged items, SALMON = withdrawn, no action required

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic and ellipsis.

- Model Code language appears upright

- Existing California amendments appear in italic

- Amended model code or new California amendments appear underlined & italic

- Repealed model code language appears upright and in strikeout

- Repealed California amendments appear in italic and strikeout

- Ellipses (…) indicate existing text remains unchanged

### ITEM 1
Chapter 5 Special occupancies, ARTICLE 517 Health Care Facilities, Section 517.31 Requirements for the Essential Electrical System

Amend sections listed below.

| OSHPD 04/25 ITEM 1 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 1-1 | 517.31(B)(3) Bypass Isolation |  |  |  | Add new exception for fire pumps to not require bypass isolation automatic transfer switches. |  |

### ITEM 2
Chapter 5, ARTICLE 517, Section 517.34 Critical Branch

Amend sections listed below.

| OSHPD 04/25 ITEM 2 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 2-1 | 517.34(A) Task Illumination, Fixed Equipment, and Select Receptacles |  |  |  | Amend (b) by deleting “where direct wired” and replacing with “where an internal battery is not provided”. |  |

### ITEM 3
Chapter 5, ARTICLE 517, Section 517.35 Equipment Branch Connection to Alternate Power Source

Amend sections listed below.

| OSHPD 04/25 ITEM 3 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 3-1 | 517.35(B) Equipment for Delayed Automatic or Manual Connection |  |  |  | Amend (5) by deleting “Automatically operated door.” and replacing with “[OSHPD 1, 2, 3, 4 & 5] Reserved” |  |

### ITEM 4
Chapter 5, ARTICLE 517, Section 517.44 Connection to Equipment Branch

Amend sections listed below.

| OSHPD 04/25 ITEM 4 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 4-1 | 517.44(A) Delayed Automatic Connections to Equipment Branch. (6) Exception # 1 |  |  |  | Amend (6) Exception # 1 to remove OSHPD 1 from the banner. |  |
| - 4-2 | 517.44(A) Delayed Automatic Connections to Equipment Branch. (6) Exception # 2 |  |  |  | Amend (6) Exception # 2 to include OSHPD 5 in the banner. |  |
| - 4-3 | 517.44(A) Delayed Automatic Connections to Equipment Branch. (7), (8) and (10) |  |  |  | Amend (7), (8) and (10) to remove OSHPD 1 from the banner. |  |
| - 4-4 | 517.44(A) Delayed Automatic Connections to Equipment Branch. (9) |  |  |  | Amend (9) to remove OSHPD 1 from the banner and delete “where direct wired” and replace with “where an internal battery is not provided.” |  |
| - 4-5 | 517.44(A) Delayed Automatic Connections to Equipment Branch. (11) |  |  |  | Add new item (11) for OSHPD 2, 4 & 5 allowing alarm systems for negative and positive pressure isolation rooms to be connected to the Delayed Automatic Connections Equipment Branch. |  |
| - 4-6 | 517.44(A) Delayed Automatic Connections to Equipment Branch. (12) |  |  |  | Add new item (12) for OSHPD 2, 4 & 5 allowing medication dispensing units to be connected to the Delayed Automatic Connections Equipment Branch. |  |
| - 4-7 | 517.44(A) Delayed Automatic Connections to Equipment Branch. (13) |  |  |  | Add new item (13) for OSHPD 2, 4 & 5 allowing medication refrigerators and freezers to be connected to the Delayed Automatic Connections Equipment Branch. |  |

### ITEM 5
Chapter 5, ARTICLE 517, Section 517.124

Amend sections listed below.

| OSHPD 04/25 ITEM 5 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 5-1 | 517.124 [OSHPD 1, 2, 4 & 5] Technology and Telecommunications Rooms |  |  |  | Amend banner to include OSHPD 2 and add additional California Building Code section reference. |  |

### ITEM 6
Chapter 6 Special equipment, ARTICLE 695 Fire Pumps

Amend sections listed below.

| OSHPD 04/25 ITEM 6 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 6-1 | 695.3 Power Source(s) for Electric Motor-Driven Fire Pumps |  |  |  | Amend banner to delete OSHPD “1R” and to include “surgical clinics only” for OSHPD 3. Include “Essential Electrical System” before the acronym EES. Delete “generator” and replace with “power source”. |  |
| - 6--2 | 695.3(G) Power Source Selection |  |  |  | Repeal the requirement to comply with 517.31(B)(3) for fire pump automatic transfer switches (ATS). |  |