# INITIAL EXPRESS TERMS
FOR PROPOSED BUILDING STANDARDS
OF THE DEPARTMENT OF HEALTH CARE ACCESS AND INFORMATION/
OFFICE OF STATEWIDE HOSPITAL PLANNING AND DEVELOPMENT
REGARDING THE 2025 CALIFORNIA ELECTRICAL CODE,
CALIFORNIA CODE OF REGULATIONS, TITLE 24, PART 3
(OSHPD 04/25)

The state agency shall draft the regulations in plain, straightforward language, avoiding technical terms as much as possible and using a coherent and easily readable style. The agency shall draft the regulation in plain English. A notation shall follow the express terms of each regulation listing the specific statutes authorizing the adoption and listing specific statutes being implemented, interpreted, or made specific (Government Code Section 11346.2(a)(1)).

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic and ellipsis.

## LEGEND for EXPRESS TERMS (Based on model codes - Parts 2, 2.5, 3, 4, 5, 7, 9, 10)

- Model Code language appears upright

- Existing California amendments appear in italic

- Amended model code or new California amendments appear underlined & italic

- Repealed model code language appears upright and in strikeout

- Repealed California amendments appear in italic and strikeout

- Ellipses ( …) indicate existing text remains unchanged

## INITIAL EXPRESS TERMS

### ITEM 1
Chapter 5 Special Occupancies
ARTICLE 517 Health Care Facilities

517.31 Requirements for the Essential Electrical System.

…

(B) Transfer switches. Transfer switches shall be in accordance with one of the following:

(1) The number of transfer switches to be used shall be based on reliability and design. Each branch of the essential electrical system shall have one or more transfer switches.

(2) One transfer switch shall be permitted to serve one or more branches in a facility with a continuous load on the switch of 150 kVA (120 kW) or less. [99:6.7.6.2.1.4]

…

(1) Optional Loads. Loads served by the generating equipment not specifically named in this article shall be served by their own transfer switches such that the following conditions apply:

…

(2) Contiguous Facilities. Hospital power sources and alternate power sources shall be permitted to serve the essential electrical systems of contiguous or same site facilities.

(3) Bypass Isolation. [OSHPD 1 & 2 (facilities complying with Article 517.40(B),3 (surgical clinics), 4, & 5] All automatic transfer switches shall be provided with an in-phase monitor relay and shall have provisions for electrically bypassing and isolating the transfer switch. The by-pass switch shall be capable of by-passing loads to the emergency source or normal source if the selected by-pass source voltage is available.

Exception: Bypass Isolation Automatic Transfer Switches shall not be required for fire pumps.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Section 1418.22, 129675-130079

### ITEM 2
Chapter 5 Special Occupancies
ARTICLE 517 Health Care Facilities

517.34 Critical Branch.

(A) Task Illumination, Fixed Equipment, and Select Receptacles. The critical branch shall supply power for task illumination, fixed equipment, select receptacles, and select power circuits serving the following spaces and functions related to patient care:

…

(11) [OSHPD 1, 2, 3, 4 & 5] The following equipment:

a. Electric clocks required by California Building Code, where direct wired.

b. Sensor-operated fixtures required by California Plumbing Code, where direct wired where an internal battery is not provided.

…

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Section 1418.22, 129675-130079

### ITEM 3
Chapter 5 Special Occupancies
ARTICLE 517 Health Care Facilities

517.35 Equipment Branch Connection to Alternate Power Source. ...

(B) Equipment for Delayed Automatic or Manual Connection. …

…

(5) Automatically operated door. [OSHPD 1, 2, 3, 4 & 5] Reserved.

…

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Section 1418.22, 129675-130079

### ITEM 4
Chapter 5 Special Occupancies
ARTICLE 517 Health Care Facilities

517.44 Connection to Equipment Branch. The equipment branch shall be installed and connected to the alternate power sources such that equipment described in 517.35(A)(6) is automatically restored to operation at appropriate time-lag intervals flowing the energizing of the life safety and critical branches [99:6.7.5.1.4.2(A)]

[OSHPD 2, 4 & 5] The equipment branch shall be installed and connected to the alternate power source such that equipment described in 517.44(A) is automatically restored to operation at appropriate time-lag intervals following the energizing of the life safety. [99:6.7.5.1.4.2(A)]

…

(A) Delayed Automatic Connections to Equipment Branch.  The following equipment shall be permitted to be connected to the equipment branch and shall be arranged for delayed automatic connection to the alternate power source:

(1) Task illumination and select receptacles in the following: [99:6.7.6.2.1.6(D)(1)]

a. Patient care spaces [99:6.7.6.2.1.6(D)(1)(a)] [OSHPD 5] Receptacles not required for psychiatric patient beds. Follow 517.18(B) Exception No. 4 requirements if receptacles are provided.

b. Medication preparation spaces [99:6.7.6.2.1.6(D)(1)(b)]

c. Pharmacy dispensing space [99:6.7.6.2.1.6(D)(1)(c)]

d. Nurses' stations - unless adequately lighted by corridor luminaires [99:6. 7 .6.2. l.6(D)(1)(d)]

(2) Supply, return, and exhaust ventilating systems for airborne infectious isolation rooms [99:6.7.6.2.1.6(D)(2)]

(3) Sump pumps and other equipment required to operate for the safety of major apparatus and associated control systems and alarms [99:6.7.6.2.1.6(D)(3)]

(4) Smoke control and stair pressurization systems [99:6. 7.6.2.1.6(D)(4)]

(5) Kitchen hood supply or exhaust systems, or both, if required to operate during a fire in or under the hood [99:6. 7.6.2.1.6(D)(5)]

(6) Nurse call systems [99:6.7.6.2.1.6(D)(6)]

[OSHPD 1, 2, 4 & 5] Exception No. 1: Battery powered components of wireless emergency nurse call systems complying with the latest edition of ANSI/UL 1069, Standard for Hospital Signaling and Nurse Call Equipment.

[OSHPD 2, & 4 & 5] Exception No. 2: Existing nurse call systems may remain on the life safety branch.

(7) [OSHPD 1, 2, 4 & 5] Selected receptacles in patient rooms or corridors so that any patient bed can be reached with a fifty (50) foot extension cord.

(8) [OSHPD 1, 2, 4 & 5] Task lighting and at least one receptacle in electrical and mechanical rooms.

(9) [OSHPD 1, 2, 3, 4 & 5] Sensor-operated fixtures required by the California Plumbing Code, where direct wired where an internal battery is not provided.

(10) [OSHPD 1, 2, 4 & 5] Equipment as required in the Essential Plumbing Provisions of the California Plumbing Code.

(11) [OSHPD 2, 4 & 5] Alarm systems for monitoring negative pressure isolation rooms and positive pressure isolation rooms.

(12) [OSHPD 2, 4 & 5] Medication dispensing units.

(13) [OSHPD 2, 4 & 5] Medication refrigerators and freezers.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Section 1418.22, 129675-130079

### ITEM 5
Chapter 5 Special Occupancies
ARTICLE 517 Health Care Facilities

517.124 [OSHPD 1, 2, 4 & 5] Technology and Telecommunications Rooms. Where technology or telecommunications rooms are provided in accordance with Section 1224.5 or 1225.5.1.1 of the California Building Code, the following requirements shall apply:

….

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Section 1418.22, 129675-130079

### ITEM 6
Chapter 6 Special Equipment
ARTICLE 695 Fire Pumps

695.3 Power Source(s) for Electric Motor-Driven Fire Pumps. Electric motor-driven fire pumps shall have a reliable source of power. [OSHPD 1, 1R, 2, 3 (surgical clinics only), 4 & 5] Such reliable source of power shall consist of a normal source and an onsite Essential Electrical System (EES) power source  generator as the alternate source.

..

G) Power Source Selection. Selection of power source shall be performed by a transfer switch listed for fire pump service. [20:10.8.1.3.1] [OSHPD 1, 2 (facilities complying with Article 517.40(B), 4 & 5] (with critical care spaces)] Transfer switch shall comply with Article 517.31(B)(3).

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Section 1418.22, 129675-130079