# COMMISSION ACTION MATRIX
Building Fire and Other – Structural Design/Lateral Forces ad-hoc (BFO/SDLF) CODE ADVISORY COMMITTEE – February 17-18, 2026

## 2025 CALIFORNIA BUILDING CODE, TITLE 24, PART 2 VOL. 2
AGENCY: OFFICE OF STATEWIDE HOSPITAL PLANNING AND DEVELOPMENT, OSHPD 03/25

### LEGEND:

CAC Actions: Approve, Disapprove, Approve as Amended, Further Study Required

Agency Responses: Accept, Disagree, Withdraw

CBSC Actions: Approve, Disapprove, Approve as Amended, Further Study Required

Matrix Paper Color (for commission action only): GREEN = uncontested items, YELLOW = challenged items, SALMON = withdrawn, no action required

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic and ellipsis.

- Model Code language appears upright

- Existing California amendments appear in italic

- Amended model code or new California amendments appear underlined & italic

- Repealed model code language appears upright and in strikeout

- Repealed California amendments appear in italic and strikeout

- Ellipses (…) indicate existing text remains unchanged

### ITEM 1
CHAPTER 16A STRUCTURAL DESIGN

Amend sections listed below.

| OSHPD 03/25 ITEM 1 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 1-1 | 1603A.1.5 Earthquake design data. |  |  |  | Amend adding requirements to the information related to seismic loads required by this section to be shown on construction documents. Coordinated with DSA. |  |
| - 1-2 | 1603A.1.6 Geotechnical information. |  |  |  | Amend adding requirements to the information related to seismic loads required by this section to be shown on construction documents. Coordinated with DSA. |  |
| - 1-3 | 1605A.1 General. |  |  |  | Amend adding a language that the use of Exception 2 of ASCE 7 Section 2.4.5 is not permitted because adjustments to the allowable yield strength of steel is made in TMS so use of this exception for masonry is not required. |  |
| - 1-4 | TABLE 1607A.1 MINIMUM UNIFORMLY DISTRIBUTED LIVE LOADS, L0, AND MINIMUM CONCENTRATED LIVE LOADS |  |  |  | Amend to restore requirements which were inadvertently omitted from recent adoptions of the code but have been historically adopted and enforced by OSHPD. |  |
| - 1-5 | 1617A.1.3 Reserved. ASCE 7, Section 11.2 [OSHPD 1 & 4] |  |  |  | Add definition of “absolute acceleration” to the modifications to ASCE 7 Section 11.2 required by OSHPD 1 and 4. |  |
| - 1-6 | 1617A.1.5 Reserved. ASCE 7 Section 12.2.3.2 [OSHPD 1 & 4] |  |  |  | Add section modifying ASCE 7 for scopes withing OSHPD 1 and 4 authority, removing the words “in addition to amplification by item (d)” from the requirements of ASCE 7 Section 12.2.3.2 (g). |  |
| - 1-7 | 1617A.1.11a ASCE 7, Section 12.8.1.1 [OSHPD 1 & 4] |  |  |  | Add new section modifying ASCE 7 to clarify use of ASCE 7 Section 12.8.1.1 Method 1. |  |
| - 1-8 | 1617A.1.18a ASCE 7 Section 13.3.1.5. [OSHPD 1 & 4] |  |  |  | Add new section modifying the requirements of ASCE 7 Section 13.3.1.5 in line with the target reliability of ASCE 7 Section 1.3 for risk category IV buildings. |  |
| - 1-9 | 1617A.1.37a ASCE 7, Section 18.4 [OSHPD 1 & 4] |  |  |  | Add new section modifying the requirements of ASCE 7 Section 18.4.1 for consistency with requirements in ASCE 7 Section 16.4.1.2. |  |

### ITEM 2
CHAPTER 17A SPECIAL INSPECTIONS AND TESTS

Amend section 1705A.5.5.

| OSHPD 03/25 ITEM 2 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 2-1 | 1705A.5.5 Structural glued laminated and cross-laminated timber. |  |  |  | Amend to repeal language related to sourcing requirements. Coordinated with DSA. |  |

### ITEM 3
CHAPTER 35 REFERENCED STANDARDS

Amend the referenced standard listed below.

| OSHPD 03/25 ITEM 3 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 3-1 | ACI 318—19 (22): Building Code Requirements for Structural Concrete |  |  |  | Adopt reapproved version of the ACI 318-19 standard. Coordinated with DSA. |  |