# INITIAL EXPRESS TERMS
FOR PROPOSED BUILDING STANDARDS
OF THE DEPARTMENT OF HEALTH CARE ACCESS AND INFORMATION/
OFFICE OF STATEWIDE HOSPITAL PLANNING AND DEVELOPMENT
REGARDING THE 2025 CALIFORNIA BUILDING CODE
CALIFORNIA CODE OF REGULATIONS, TITLE 24, PART 2, VOLUME 2
(OSHPD03/25)

The state agency shall draft the regulations in plain, straightforward language, avoiding technical terms as much as possible and using a coherent and easily readable style. The agency shall draft the regulation in plain English. A notation shall follow the express terms of each regulation listing the specific statutes authorizing the adoption and listing specific statutes being implemented, interpreted, or made specific (Government Code Section 11346.2(a)(1)).

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic and ellipsis.

## LEGEND for EXPRESS TERMS (Based on model codes - Parts 2, 2.5, 3, 4, 5, 7, 9, 10)

- Model Code language appears upright

- Existing California amendments appear in italic

- Amended model code or new California amendments appear underlined & italic

- Repealed model code language appears upright and in strikeout

- Repealed California amendments appear in italic and strikeout

- Ellipses ( …) indicate existing text remains unchanged

## INITIAL EXPRESS TERMS

### ITEM 1
CHAPTER 16A STRUCTURAL DESIGN

...

#### SECTION 1603A—CONSTRUCTION DOCUMENTS

...

1603A.1.5 Earthquake design data. The following information related to seismic loads shall be shown, regardless of whether seismic loads govern the design of the lateral force-resisting system of the structure:

- Project location.

- 1. Risk category.

- 2. Seismic importance factor, Ie.

- 3. Spectral response acceleration parameters, SS and S1.

- 4. Site class.

- 5. Design spectral response acceleration parameters, SDS and SD1, MPRS spectrum or Site-specific response spectrum.

- Design spectral response acceleration, SDS, for non-structural components.

- 6. Seismic design category.

- 7. Basic seismic force-resisting system(s). in each direction.

8.	Design base shear(s).

9.	Seismic response coefficient(s), CS.

10.	Response modification coefficient(s), R. Seismic force-resisting system factors R, Cd, and Ω0 in each direction.

- Seismic response coefficient, Cs, in each direction.

- Design base shear, V, in each direction.

- Design earthquake displacement, δDE, in each direction.

- Redundancy factor, ρ, in each direction.

- 11. Analysis procedure used.

- Fundamental period, T, in each direction.

- Approximate fundamental period, Ta, in each direction.

- 12.Applicable horizontal structural irregularities.

- 13.Applicable vertical structural irregularities.

- 14.Location of base as defined in ASCE 7, Section 11.2.

- Grade plane level or level of the seismic base.

1603A.1.5.1 Connections. Connections that resist design seismic forces shall be designed and detailed on the design drawings.

1603A.1.6 Geotechnical information. The design load-bearing values of soils shall be shown on the construction documents. The construction documents shall provide a description of the foundation system and the design load-bearing values of soils and/or deep foundations elements. In Seismic Design Categories C through F, the capacity of the soil/foundation for seismic load cases shall be included.

…

#### SECTION 1605A—LOAD COMBINATIONS

1605A.1 General. Buildings and other structures and portions thereof shall be designed to resist the strength load combinations specified in ASCE 7, Section 2.3, the allowable stress design load combinations specified in ASCE 7, Section 2.4, or the alternative allowable stress design load combinations of Section 1605A.2.

Exceptions:

- The modifications to load combinations of ASCE 7, Section 2.3, ASCE 7, Section 2.4 and Section 1605A.2 specified in ASCE 7 Chapters 18 and 19 shall apply. [OSHPD 1 & 4] Exception 2 of ASCE 7 Section 2.4.5 shall not be permitted.

…

#### SECTION 1607A—LIVE LOADS

…

TABLE 1607A.1—MINIMUM UNIFORMLY DISTRIBUTED LIVE LOADS, L0, AND MINIMUM CONCENTRATED LIVE LOADS

|  | OCCUPANCY OR USE | UNIFORM (psf) | CONCENTRATED (pounds) | ALSO SEE SECTION |
| --- | --- | --- | --- | --- |
| … | … | … |  | … |
|  | Corridors above first floor | 80 | 1,000 |  |
|  | Operating rooms, laboratories a | 60 | 1,000 |  |
|  | Patient rooms | 40 | 1,000 |  |
|  | Mechanical and electrical areas including open areas around equipment | 50 |  |  |
| 18. Hospitals [OSHPD 1 & 4] | Storage Light Heavy | 125 250 |  | — |
|  | Dining areas not used for assembly | 100 | 1,000 |  |
|  | Kitchen and serving areas | 50 | 1,000 |  |
| … | … | … | … | … |

For SI: 1 inch = 25.4 mm, 1 square inch = 645.16 mm2, 1 square foot = 0.0929 m2, 1 pound per square foot = 0.0479 kN/m2, 1 pound = 0.004448 kN.

a. Live load reduction is not permitted.

…

#### SECTION 1617A—MODIFICATIONS TO ASCE 7

…

1617A.1.2 ASCE 7, Section 11.1.3. Replace last paragraph of ASCE 7, Section 11.1.3, by the following:

Non-building structures similar to buildings shall be designed and detailed in accordance with Chapter 12.

1617A.1.3 Reserved. ASCE 7, Section 11.2 [OSHPD 1 & 4] Modify ASCE 7 Section 11.2 by adding the following:

11.2 DEFINITIONS

The following definitions apply only to the seismic provisions of Chapters 11 through 22 of this standard.

ABSOLUTE ACCELERATION: absolute acceleration is the total acceleration of an object relative to a universal or "fixed" reference frame.

…

1617A.1.5 Reserved. ASCE 7 Section 12.2.3.2 [OSHPD 1 & 4] Modify ASCE 7 Section 12.2.3.2 (g) with the following:

Modify the last sentence “… and Section 12.10.3.3, in addition to amplification by item (d),” by deleting “…in addition to amplification by item (d).”

…

1617A.1.11 ASCE 7, Section 12.7.2. ...

...

1617A.1.11a ASCE 7, Section 12.8.1.1 [OSHPD 1 & 4] Modify ASCE 7 Section 12.8.1.1, as follows:

…

Method 1: The seismic response coefficient, Cs, shall be determined in accordance with Equation (12.8-2). The values of Cs need not exceed the value computed in accordance with Equation (12.8-2).

Cs=SaRIe  			(12.8-2)

…

1617A.1.12 ASCE 7, Section 12.10.2.1. ...

…

1617A.1.18a ASCE 7 Section 13.3.1.5. [OSHPD 1 & 4] Modify ASCE 7 Section 13.3.1.5 with the following:

- Modify the sentence after Equation (13.3-7), “where ai is the maximum acceleration at level i obtained from the nonlinear response history analysis at the Design Earthquake ground motion.” by adding the word “absolute” before acceleration.

- Add the following at the end of the section. For base-isolated structures designed using nonlinear response history analysis, a smaller lower limit of Fp is permitted, but shall not be less than one-half of that determined by Equation (13.3-3).

…

1617A.1.37a ASCE 7, Section 18.4 [OSHPD 1 & 4] Replace last paragraph ASCE 7, Section 18.4.1 with the following:

The maximum drift at MCER shall neither exceed 3%, nor the drift limits specified in Table 12.12-1 times the smaller of 1.5R∕Cd and 1.9 2.0. Cd and R shall be taken from Table 12.2-1 for the building framing under consideration.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code Sections 129675-130079

### ITEM 2
CHAPTER 17A SPECIAL INSPECTIONS AND TESTS

...

#### SECTION 1705A—REQUIRED SPECIAL INSPECTION AND TESTS

…

1705A.5.5 Structural glued laminated and cross-laminated timber. …

Exception: Special Inspection is not required for non-custom prismatic glued laminated members identified on drawings and sourced from stock or general inventory of 5 1/2-inch maximum width and 18-inch maximum depth, and with a maximum clear span of 32 feet, manufactured and marked in accordance with ANSI/APA A190.1 Section 14.1 for noncustom members.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code Sections129675-130079

### ITEM 3
CHAPTER 35 REFERENCED STANDARDS

…

#### ACI	American Concrete Institute ...

…

318—19 (22): Building Code Requirements for Structural Concrete

…

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code Sections 129675-130079