# COMMISSION ACTION MATRIX
BUILDING, FIRE AND OTHER – STRUCTURAL DESIGN/LATERAL FORCES AD-HOC (bfo/sdlf) CODE ADVISORY COMMITTEE – February 17-18, 2026

## 2025 CALIFORNIA EXISTING BUILDING CODE, TITLE 24, PART 10
AGENCY: office of statewide health planning and development, oshpd 07/25

### LEGEND:

CAC Actions: Approve, Disapprove, Approve as Amended, Further Study Required

Agency Responses: Accept, Disagree, Withdraw

CBSC Actions: Approve, Disapprove, Approve as Amended, Further Study Required

Matrix Paper Color (for commission action only): GREEN = uncontested items, YELLOW = challenged items, SALMON = withdrawn, no action required

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic and ellipsis.

- Model Code language appears upright

- Existing California amendments appear in italic

- Amended model code or new California amendments appear underlined & italic

- Repealed model code language appears upright and in strikeout

- Repealed California amendments appear in italic and strikeout

- Ellipses (…) indicate existing text remains unchanged

### ITEM 1
CHAPTER 3A PROVISION FOR ALL COMPLIANCE METHODS

Amend sections listed below.

| OSHPD 07/25 ITEM 1 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 1-1 | 304A.3.5 Modifications to ASCE 41-13 for SPC-2 and SPC-4D. |  |  |  | Amend to coordinate with proposals in ITEMS 1-3 and 1-4. |  |
| - 1-2 | 304A.3.5.13 ASCE 41-13 Section 10.7.1.1. |  |  |  | Amend to clarify that only flexure controlled and shear controlled horizontal wall segments or spandrels, reinforced with closed hoops or stirrups anchored to the longitudinal reinforcement top and bottom for shear wall coupling beams in ASCE 41 are permitted to be classified as coupling beams. |  |
| - 1-3 | 304A.3.5.16 ASCE 41-13 Chapter 13. |  |  |  | Add new section for Penthouse Structures as the code is not clear how existing penthouse structures are to be evaluated as related to seismic upgrades of existing hospital buildings from SPC-1 to SPC-4D. |  |
| - 1-4 | 304A.3.5.1617 304A.3.5.1718 |  |  |  | Renumber these sections to coordinate with changes proposed in ITEM 1-3. |  |
| - 1-5 | 304A.3.6 Modifications to ASCE 41-23. |  |  |  | Amend to coordinate with proposals in ITEMS 1-6 and 1-7. |  |
| - 1-6 | 304A.3.6.9 ASCE 41-23 Chapter 13. |  |  |  | Add new section for Penthouse Structures. This amendment aligns the performance level for evaluation and retrofit of small rooftop penthouse structures to the same performance level permitted for existing SPC-1 buildings upgraded to the SPC-4D performance level for non SPC-1 buildings regardless of which version of ASCE 41 is used for the evaluation/retrofit. |  |
| - 1-7 | 304A.3.6.910 ASCE 41-23 Chapter 16 and 17. |  |  |  | Renumber this section to coordinate with changes proposed in ITEM 1-6. |  |