# INITIAL EXPRESS TERMS
FOR PROPOSED BUILDING STANDARDS
OF THE OFFICE OF STATE FIRE MARSHAL
REGARDING THE 2025 CALIFORNIA WILDLAND-URBAN INTERFACE CODE,
CALIFORNIA CODE OF REGULATIONS, TITLE 24, PART 7
(SFM 04/25)

The state agency shall draft the regulations in plain, straightforward language, avoiding technical terms as much as possible and using a coherent and easily readable style. The agency shall draft the regulation in plain English. A notation shall follow the express terms of each regulation listing the specific statutes authorizing the adoption and listing specific statutes being implemented, interpreted, or made specific (Government Code Section 11346.2(a)(1)).

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic, highlight and ellipsis.

## LEGEND for EXPRESS TERMS (Based on model codes - Parts 2, 2.5, 3, 4, 5, 7, 9, 10)

- Model Code language appears upright

- Existing California amendments appear in italic

- Amended model code or new California amendments appear underlined & italic

- Repealed model code language appears upright and in strikeout

- Repealed California amendments appear in italic and strikeout

- Emergency Regulations language approved October 15, 2025, appears in italic, strikeout and gray highlight or italic, underlined and gray highlight

- Text which contains instructions or explanations only that are not amendments and will not be printed appears in [text within brackets]

- Ellipses ( …) indicate existing text remains unchanged

## INITIAL EXPRESS TERMS

### ITEM 1
Chapter 1 Administration

#### SUB-ITEM 1-1
Division I California Administration, Section 1.1.2 Purpose

[Part of the proposed changes in this section, identified with gray highlight, were included in the Emergency Regulations approved October 15, 2025. SFM proposes further amendments in this section that were not included in the Emergency Regulations.]

1.1.2 Purpose. The purpose of this code is to establish minimum requirements to reduce the likelihood of life and property loss due to wildfire through the use of performance and prescriptive requirements for construction and development in all Fire Hazard Severity Zones in State Responsibility Areas (SRA), and Local Responsibility Areas (LRA) designated identified by the State Fire Marshal as a High or Very High Fire Hazard Severity Zone, and LRA designated High or Very High Fire Hazard Severity Zone by a local agency pursuant to Government Code Section 51179(b). This will increase the ability of buildings located in any Fire Hazard Severity Zone within State Responsibility Areas (SRA), or Wildland-Urban Interface (WUI) Areas identified area to resist the intrusion of flames or burning embers projected by a vegetation fire and contributes to a systematic reduction in conflagration losses and reduce the likelihood of life and property loss due to a wildfire.

#### SUB-ITEM 1-2
Division II Scope and Administration, Section 101.2 Scope

[SFM proposes to amend the scoping section that has caused code user confusion.]

[A] 101.2 Scope. This code applies to building materials, systems and/or assemblies used in the exterior design and construction of new buildings located within a Wildland-Urban Interface (WUI) Area all Fire Hazard Severity Zones in State Responsibility Areas (SRA), Local Responsibility Areas (LRA) designated as a High or Very High Fire Hazard Severity Zone, or Fire Hazard Severity Zones as specified in Section 101.3.1 and contains minimum requirements to mitigate conditions that might cause a fire originating in a structure to ignite vegetation in the Wildland-Urban Interface (WUI) area, and conversely, a wildfire burning in vegetative fuels to transmit fire to buildings and threaten to destroy life, overwhelm fire suppression capabilities or result in large property losses.

#### SUB-ITEM 1-3
Division II, Section 101.3.1 Application and 101.3.1.1 Application date and where required

[The proposed amendments in these sections were included in the Emergency Regulations approved October 15, 2025, with some changes identified below and explained in the ISOR.]

101.3.1 Application. New buildings located in any Fire Hazard Severity Zone or Wildland-Urban Interface (WUI) Fire Area designated by the enforcing agency constructed after the application date shall comply with the provisions of this code. This shall include all new buildings with residential, commercial, educational, institutional or similar occupancy type use, which shall be referred to in this code as “applicable buildings,” as well as new buildings and structures accessory to those applicable buildings.

Exceptions:

- Group U occupancy accessory buildings of any size located at least 50 feet (15 240 mm) from an applicable building on the same lot.

- Group U occupancy agricultural buildings, as defined in Section 202 of the California Building Code of any size located at least 50 feet (15 240 mm) from an applicable building.

- Group C occupancy special buildings conforming to the limitations specified in Section 450.4.1 of the California Building Code.

- New accessory buildings and miscellaneous structures specified in Section 504.11 shall comply only with the requirements of that section.

- Additions to and remodels of buildings originally constructed prior to July 1, 2008.

101.3.1.1 Application date and where required. New buildings for which an application for a building permit is submitted on or after July 1, 2008, located in any Fire Hazard Severity Zone or Wildland-Urban Interface Area shall comply with this code, including all of the following areas:

All unincorporated lands designated by the State Board of Forestry and Fire Protection as State Responsibility Area (SRA) including:

Moderate Fire Hazard Severity Zones.

High Fire Hazard Severity Zones.

Very High Fire Hazard Severity Zones.

Land designated as a Very High Fire Hazard Severity Zone by cities and other local agencies.

Land designated as a wildland-urban interface area by cities and other local agencies.

Exceptions:

1. New buildings located in any Fire Hazard Severity Zone within a State Responsibility Area, for which an application for a building permit is submitted on or after January 1, 2008, shall comply with this code.

2. New buildings located in any Fire Hazard Severity Zone within a State Responsibility Area or any wildland-urban interface area designated by cities and other local agencies for which an application for a building permit is submitted on or after December 1, 2005, but prior to July 1, 2008, shall only comply with the following sections of this chapter:

2.1. Section 507 – Replacement or Repair of Roof Coverings.

2.2. Section 504.10 – Vents

101.3.1 Application. New buildings and structures with residential, commercial, educational, institutional or similar occupancy type use, which shall be referred to in this code as “applicable buildings,” as well as new buildings and structures accessory to those applicable buildings, located in any of the following:

1. All lands designated by the State Board of Forestry and Fire Protection as State Responsibility Area (SRA)

2. Lands in Local Responsibility Area (LRA) identified by the State Fire Marshal as High or Very High Fire Hazard Severity Zone.

3. Lands in the LRA designated as a High or Very-High Fire Hazard Severity Zone by a Local agency.

4. Land designated as a Wildland-Urban Interface Area by cities and other local agencies. [Item 4 was added in the Emergency Regulations approved October 15, 2025, but it is proposed to be deleted in this certifying rulemaking.]

Exceptions:

1. Group U occupancy accessory buildings of any size located at least 50 feet (15 240 mm) from an applicable building on the same lot. [Exception 1 was added in the Emergency Regulations approved October 15, 2025, but it is proposed to be deleted in this certifying rulemaking.]

2. Group U occupancy agricultural buildings, as defined in Section 202 of the California Building Code of any size located at least 50 feet (15 240 mm) from an applicable building. [Exception 2 was added in the Emergency Regulations approved October 15, 2025, but is proposed to be deleted in this certifying rulemaking.]

3. Group C occupancy special buildings conforming to the limitations specified in Section 450.4.1 of the California Building Code.

4. New accessory buildings and miscellaneous structures specified in Section 504.11 shall comply only with the requirements of that section. [Exception 4 was added in the Emergency Regulations approved October 15, 2025, but it is proposed to be deleted in this certifying rulemaking.]

#### SUB-ITEM 1-4
Division II, Section 101.5 Additions or alterations

[SFM proposes adopting section 101.5 about additions and alterations.]

101.5 Additions or alterations. Additions or alterations shall be permitted to be made to any building or structure without requiring the existing building or structure to comply with all of the requirements of this code, provided that the addition or alteration conforms to that required for a new building or structure.

Exception: Provisions of this code that specifically apply to existing conditions are retroactive.

Additions or alterations shall not be made to an existing building or structure that will cause the existing building or structure to be in violation of any of the provisions of this code nor shall such additions or alterations cause the existing building or structure to become unsafe. An unsafe condition shall be deemed to have been created if an addition or alteration will cause the existing building or structure to become structurally unsafe or overloaded; will not provide adequate access in compliance with the provisions of this code or will obstruct existing exits or access; will create a fire hazard; will reduce required fire resistance or will otherwise create conditions dangerous to human life.

#### SUB-ITEM 1-5
Division II, Section 101.6 Maintenance

[SFM proposes amending section 101.6 Maintenance to close the gaps identified in the SFM CWUI work group.]

101.6 Maintenance. Buildings, structures, landscape materials, vegetation, defensible space or and other devices or safeguards required by this code shall be maintained in conformance to the code edition under which they were constructed or required to be installed.

Landscape materials, vegetation, and defensible space shall be in conformance with this code, and an approved fire protection plan and any other applicable code or standard, such as NFPA 1140, for hazard mitigation requirements imposed by the code official at the time of site approval.

The owner or the owner’s authorized agent shall be responsible for the maintenance of buildings, structures, landscape materials and vegetation.

#### SUB-ITEM 1-6
Division II, Section 104.2.2 Alternative materials, design and methods

[SFM proposes amending section 104.2.2 to include an International Wildland-Urban Interface Code (IWUIC) errata that was omitted from the first printing of the 2024 edition.]

[A] 104.2.2 Alternative materials, design and methods. The provisions of this code are not intended to prevent the installation of any material or to prohibit any design or method not specifically prescribed by this code, provided that any such alternative is not specifically prohibited by this code and has been approved

#### Notation:

Authority: Health and Safety Code Sections 1250, 1502, 1568.02, 1569.70 - 1569.74, 1597.44 - 1597.65, 13108, 13108.5, 13114, 13143, 13143.2, 13143.6, 13145, 13146, 13211, 16022.5, 17921, 18928, 18949.2, 25500 through 25545; Government Code Sections 51176, 51177, 51178, 51179 and 51189; Public Education Code 17074.50; Public Resources Code Sections 4201 through 4204.

Reference(s): Health and Safety Code Sections 13108, 13108.5, 13113, 13113.5, 13114, 13132, 13132.7, 13133, 13135, 13143, 13143.1, 13143.2, 13143.6, 13143.9, 13145, 13146, 13210, 13211, 16022.5, 17921.

### ITEM 2
Chapter 2 Definitions

#### SUB-ITEM 2-1
Glazed Door

[SFM proposes to add a new definition]

GLAZED DOOR. An exterior door having a glazed area of 25 percent or greater of the door.

#### SUB-ITEM 2-2
Home Hardening

[The proposed definition was included in the Emergency Regulations approved October 15, 2025.]

Home Hardening. A method of utilizing construction features, building materials, and maintenance practices intended to increase a building and structure’s resistance to ignition from fire exposure, including direct flame contact, radiant heat, and embers.

#### SUB-ITEM 2-3
Local Responsibility Area (LRA)

[SFM proposes to align the definition of Local Responsibility Area with the Title 19 definition for coordination.]

LOCAL RESPONSIBILITY AREA (LRA). Those Aareas of land classified by the Board of Foresty and Fire Protection (Board) the state in which where the financial responsibility of preventing and suppressing fires wildfires is not that of the state or federal government, pursuant to Public Resources Code (PRC) section 4125. the primary responsibility of a city, county, city and county, or district. See also “State Responsibility Area (SRA).”

#### SUB-ITEM 2-4
State Responsibility Areas (SRA)

[SFM proposes to align the definition of State Responsibility Areas with the definition in Public Resources Code 4102 for coordination.]

STATE RESPONSIBILITY AREAS (SRA). Lands that are classified by the Board of Forestry pursuant to Public Resources Code Section 4125 where the financial responsibility of preventing and suppressing forest fires is primarily the responsibility of the state. Areas of the state in which the financial responsibility of preventing and suppressing fires has been determined by the Board of Foresty and Fire Protection pursuant to Public Resources Code (PRC) 4125, to be the responsibility of the state.

#### SUB-ITEM 2-5
Vegetation

[SFM proposal from the 2025 CWUI Work Group – Chapter 6 Subgroup.]

Vegetation. All plants, including trees, shrubs, grass, and perennial or annual plants.

#### SUB-ITEM 2-6
Wildland-Urban Interface Area

[SFM proposes to clarify the meaning and intent of what a Wildland-Urban Interface area is intended to mean when applying the regulations.]

WILDLAND-URBAN INTERFACE AREA (WUI). A geographical area that is in a Fire Hazard Severity Zone in State Responsibility Area (SRA), or in a Local Responsibility Area (LRA) identified by the state State Fire Marshal as a High or Very High Fire Hazard Severity Zone, or in the LRA and designated High or Very High Fire Hazard Severity Zone by a Local agency pursuant to Government Code section 51179(b).“Fire Hazard Severity Zone” in accordance with the Public Resources Code Sections 4201 through 4204 and Government Code Sections 51175 through 51189, and other areas designated by the enforcing agency to be at a significant risk from wildfires.

#### Notation:

Authority: Health and Safety Code Sections 1250, 1502, 1568.02, 1569.70 - 1569.74, 1597.44 - 1597.65, 13108, 13108.5, 13114, 13143, 13143.2, 13143.6, 13145, 13146, 13211, 16022.5, 17921, 18928, 18949.2, 25500 through 25545; Government Code Sections 51176, 51177, 51178, 51179 and 51189; Public Education Code 17074.50; Public Resources Code Sections 4201 through 4204.

Reference(s): Health and Safety Code Sections 13108, 13108.5, 13113, 13113.5, 13114, 13132, 13132.7, 13133, 13135, 13143, 13143.1, 13143.2, 13143.6, 13143.9, 13145, 13146, 13210, 13211, 16022.5, 17921.

### ITEM 3
Chapter 3 Wildland Urban Interface Areas

#### SUB-ITEM 3-1
Sections 301.1. Scope and 302.1.1 Fire Hazard Severity Zone Viewer

[This amendment provides code users with the location where to find the Fire Hazard Severity Zone maps.]

301.1 Scope. The provisions of this chapter provide methodology to establish and record wildland-urban interface areas Fire Hazard Severity Zones in accordance with California Public Resources Code (PRC) and California Government Code (GC).

…

302.1 Mapping. …

302.1.1 Fire Hazard Severity Zone (FHSZ) viewer. Fire Hazard Severity Zone maps can be viewed on the Office of the State Fire Marshal website, osfm.fire.ca.gov/what-we-do/community-wildfire-prepardness-and-mitigation/fire-hazard-severity-zones.

Contact the Local agency for information on a specific area located within the Local Responsibility Area.

#### SUB-ITEM 3-2
Section 302.2 Review of Fire Hazard Severity Zones

[SFM proposes to clean up model code language and replace it with California terms to ensure understandability and application.]

302.2 Review of wildland-urban interface areas Fire Hazard Severity Zones. The code official shall reevaluate and recommend modification to the wildland-urban interface areas in accordance with Section 302.1 on a 5-year basis or more frequently as deemed necessary by the legislative body. The State Fire Marshal shall periodically review the areas in the state identified as fire hazard severity zones Fire Hazard Severity Zones and, as necessary, shall make recommendations relative to fire hazard severity zones Fire Hazard Severity Zones. This review shall coincide with the review of state responsibility area State Responsibility Area lands every five years and, when possible, fall within the time frames for the county’s general plan update.

#### SUB-ITEM 3-3
Section 302.3 Local Designation

[SFM proposes adding a new section to increase awareness.]

302.3 Local designation. A local agency shall adopt by ordinance and designate moderate, high, and very high fire hazard severity zones in its jurisdiction within 120 days of receiving recommendations from the State Fire Marshal.  A local agency may, at its discretion, include areas not identified and may only increase the level of fire hazard severity in accordance with Government Code Section 51179.

#### Notation:

Authority: Health and Safety Code Sections 1250, 1502, 1568.02, 1569.70 - 1569.74, 1597.44 - 1597.65, 13108, 13108.5, 13114, 13143, 13143.2, 13143.6, 13145, 13146, 13211, 16022.5, 17921, 18928, 18949.2, 25500 through 25545; Government Code Sections 51176, 51177, 51178, 51179 and 51189; Public Education Code 17074.50; Public Resources Code Sections 4201 through 4204.

Reference(s): Health and Safety Code Sections 13108, 13108.5, 13113, 13113.5, 13114, 13132, 13132.7, 13133, 13135, 13143, 13143.1, 13143.2, 13143.6, 13143.9, 13145, 13146, 13210, 13211, 16022.5, 17921.

### ITEM 4
Chapter 5 Special Building Construction Regulations

#### SUB-ITEM 4-1
Section 503 and Section 503.1 General

[Proposed changes in this section identified with gray highlight were included in the Emergency Regulations approved October 15, 2025. The rest of the proposal is from the 2025 CWUI Work Group – Ignition resistant materials and weathering Subgroup – early adopting provisions from the ICC 2024–2026 Code Development Cycle, Group A as SFM amendments.]

SECTION 503 IGNITION-RESISTANT CONSTRUCTION AND MATERIAL

503.1 General. Buildings and structures hereafter constructed, modified or relocated into or within wildland-urban interface areas shall meet the construction requirements in accordance with Chapter 5. Materials required to be ignition-resistant building materials shall comply with the requirements of Section 503.2. Materials required to be fire-retardant-treated wood roof coverings shall comply with the requirements of Section 503.3. Where this code requires fire-resistance-rated construction, fire-resistance ratings shall be determined in accordance with Section 503.4.

Exceptions:

1. New accessory buildings and miscellaneous structures complying with Section 504.11.

2. Additions to and remodels of buildings originally constructed prior to July 1, 2008.

32. Group C occupancy special buildings conforming to the limitations specified in Section 450.4.1 of the California Building Code.

#### SUB-ITEM 4-2
Sections 503.2, 503.2.1, 503.2.1.1, 503.2.1.1.1, 503.2.1.1.2, 503.2.2, 503.2.3, 503.2.3.1, 503.2.3.2, 503.2.3.3, 503.2.3.3.1, 503.2.3.3.2, 503.2.3.3.3, 503.2.3.3.4, 502.5, 503.3, 503.4, 503.5, 503.5.1, 503.5.2, 503.5.3, 503.5.4

[SFM proposal from the 2025 CWUI Work Group – Ignition resistant materials and weathering Subgroup – is to early adopt provisions from the ICC 2024–2026 Code Development Cycle, Group A as SFM amendments and propose additional amendments.]

503.2 Ignition-resistant building material. Ignition-resistant building materials shall be designed for exterior use and weather exposure and shall comply with any one of the requirements in Section 503.2.1 through 503.2.4.3.3 503.2.3.3.3. [the following is relocated from Section 503.2.5] Use of paints, coatings, stains or other surface treatments are not an approved method of protection as required in this chapter.

503.2.1 Noncombustible material. Noncombustible material shall comply with the requirements in Section 501.4 Sections 503.2.1.1 and 503.2.1.2.

501.4 503.2.1.1 Noncombustibility tests. The tests indicated in Section 501.4.1 503.2.1.1.1 shall serve as criteria for acceptance of noncombustible building materials. The term “noncombustible” does not apply to the flame spread characteristics of interior finish or trim materials. A material shall not be classified as a noncombustible building construction material if it is subject to an increase in combustibility or flame spread beyond the limitations herein established through the effects of age, moisture or other atmospheric conditions.

501.4.1 Noncombustible materials 503.2.1.1.1 Testing. Materials required to be noncombustible shall be tested in accordance with ASTM E136 and pass the test. Alternately, materials required to be noncombustible shall be tested in accordance with ASTM E2652 and comply with the acceptance criteria prescribed by ASTM E136.

Exception: Materials having a structural base of noncombustible material as determined in accordance with ASTM E136, or with ASTM E2652 using the acceptance criteria prescribed by ASTM E136, and a surfacing of not more than 0.125 inch (3.18 mm) in thickness having a flame spread index not greater than 50 when tested in accordance with ASTM E84 or UL 723 shall be acceptable as noncombustible.

503.2.1.1.2 Additional requirements. Materials required to be noncombustible for reduced clearances to flues, heating appliances or other sources of high temperature shall be material conforming to the requirements of ASTM E136.

503.2.2 Fire-retardant-treated wood. Fire-retardant-treated wood shall be identified for exterior use and shall exposed to weathering in accordance with Method A in ASTM D2898 and meet the requirements of Section 2303.2 of the California Building Code. Fire-retardant-treated wood shall be identified for exterior use.

503.2.4 503.2.3 Other ignition-resistant building material. Material Materials other than noncombustible materials and fire-retardant-treated wood materials shall be tested on the front and back faces in accordance with the extended ASTM E84 or UL 723 test, for a total test period of 30 minutes, or with the ASTM E2768 test. The materials shall bear identification showing the fire test results. Panel products shall be tested with a ripped or cut longitudinal gap of 1/8 inch (3.2 mm). The materials, when tested in accordance with the test procedures set forth in ASTM E84 or UL 723 for a test period of 30 minutes, or with ASTM E2768, shall comply with Sections 503.2.4.1 503.2.3.1 through 503.2.4.3 503.2.3.3.

Exception: Materials composed of a combustible core and a noncombustible exterior covering made from either aluminum at a minimum 0.019 inch (0.48 mm) thickness or corrosion-resistant steel at a minimum 0.0149 inch (0.38 mm) thickness shall not be required to be tested with a ripped or cut longitudinal gap.

503.2.4.1 503.2.3.1 Flame spread. The material shall exhibit a flame spread index not exceeding 25.

503.2.4.2 503.2.3.2 Flame front. The material shall exhibit a flame front that does not progress more than 10 feet 6 inches (3200 mm) beyond the centerline of the burner at any time during the test.

503.2.4.3 503.2.3.3 Weathering. Ignition-resistant building The materials material shall maintain their its performance in accordance with this section under conditions of use. The materials shall meet the performance requirements for weathering (including exposure to temperature, moisture and ultraviolet radiation) contained in Sections 503.2.4.3.1 503.2.3.3.1 through 503.2.4.3.3 503.2.3.3.4, as applicable to the materials and conditions of use.

503.2.4.3.1 503.2.3.3.1 Evaluation requirements for weathering. Fire-retardant-treated wood-plastic composite materials and plastic lumber materials shall be evaluated after weathering in accordance with Method A “Test Method for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing” in ASTM D2898.

503.2.4.3.2 503.2.3.3.2 Wood-plastic composite materials. Wood-plastic composite materials shall also demonstrate acceptable fire performance after weathering by the following procedure: first testing in accordance with ASTM E1354 at an incident heat flux of 50 kW/m² in the horizontal orientation, then weathering in accordance with ASTM D7032 and then retesting in accordance with ASTM E1354 and exhibiting an increase of no more than 10 percent in peak rate of heat release when compared to the peak heat release rate of the nonweathered material.

503.2.4.3.3 503.2.3.3.3 Plastic lumber materials. Plastic lumber materials shall also demonstrate acceptable fire performance after weathering by the following procedure: first testing in accordance with ASTM E1354 at an incident heat flux of 50 kW/m² in the horizontal orientation, then weathering in accordance with ASTM D6662 and then retesting in accordance with ASTM E1354 and exhibiting an increase of no more than 10 percent in peak rate of heat release when compared to the peak heat release rate of the nonweathered material.

503.2.5 Surface treatment protection. [the following is relocated to Section 503.2] Use of paints, coatings, stains or other surface treatments are not an approved method of protection as required in this chapter.

503.2.3.3.4 Weathering for other building materials. Materials other than noncombustible materials, fire-retardant-treated wood materials, wood-plastic composite materials and plastic lumber materials shall demonstrate that they retain the fire performance required by Section 503.2.3 after weathering in accordance with Test Method A in ASTM D2898.

503.2.3 503.3 Fire-retardant-treated wood roof coverings. Roof assemblies containing fire-retardant-treated wood shingles and shakes shall comply with the requirements of Section 1505.6 of the California Building Code and shall be classified as Class A roof assemblies as required in Section 1505.2 of the California Building Code.

501.3 503.4 Fire-resistance-rated construction. Where this code requires 1-hour fire-resistance-rated construction, the fire-resistance rating of building elements, components or assemblies shall be determined in accordance with the test procedures set forth in ASTM E119 or UL 263.

Exceptions:

- The fire-resistance rating of building elements, components or assemblies based on the prescriptive designs prescribed in Section 721 of the California Building Code.

- The fire-resistance rating of building elements, components or assemblies based on the calculation procedures in accordance with Section 722 of the California Building Code.

503.3 503.5 Standards of quality. Building material, systems, assemblies and methods of construction shall be tested in accordance with the standards specified in Chapter 5.

503.3.1 503.5.1 Qualification by testing. Material and material assemblies tested in accordance with the requirements of Section 503 shall be accepted for use when the results and conditions of those tests are met. Product evaluation testing of material and material assemblies shall be approved or listed by the State Fire Marshal or identified in a current report issued by an approved agency.

503.3.2 503.5.2 Approved agency. Product evaluation testing shall be performed by an approved agency in accordance with Section 1703 of the California Building Code. The scope of accreditation for the approved agency shall include building product compliance with this code.

503.3.3 503.5.3 Labeling. Material and material assemblies tested in accordance with the referenced standards shall bear an identification label showing the fire test results. That identification label shall be issued by a testing and/or inspecting agency approved by the State Fire Marshal.

1.	Identification mark of the approved testing and/or inspecting agency.

2.	Contact and identification information of the manufacturer.

3.	Model number or identification of the product or material.

4.	Pre-test weathering specified in this chapter.

5.	Compliance standard as described under Chapter 7.

503.3.4 503.5.4 Fire-retardant-treated wood shingles and shakes. Fire-retardant-treated wood shingles and shakes shall be approved and listed by the State Fire Marshal in accordance with Section 208(c), Title 19 California Code of Regulations.

#### SUB-ITEM 4-3
Section 504.2 Roof Assembly

[SFM proposal from the 2025 CWUI Work Group – Roofs Subgroup.]

504.2 Roof assembly. Roofs shall have a roof assembly that complies with classified as a Class A fire classification when tested in accordance with ASTM E108 or UL 790.

Exceptions: The following roof assemblies are exempt from testing and shall be considered as equivalent to the Class A fire classification permitted without testing:

    - Roof assemblies with coverings of brick, masonry or an exposed concrete roof deck.

    - Roof assemblies with ferrous or copper shingles or sheets, metal sheets and shingles, clay or concrete roof tile or slate installed on noncombustible decks or ferrous, copper or metal sheets installed without a roof deck on noncombustible framing.

    - Roof assemblies with minimum 16 oz/sq ft (0.0416 kg/m2) copper sheets installed over combustible roof decks.

    - Roof assemblies of with slate roof covering installed over ASTM D226, Type II or ASTM D4869, Type IV underlayment over combustible decks.

#### SUB-ITEM 4-4
Section 504.2.1 Roof covering voids and subsections

[SFM proposal from the 2025 CWUI Work Group – Roofs Subgroup. Delete and replace sections with new text that provides clarity to the requirements of roof coverings with an airspace under the roof coverings.]

504.2.1 Roof covering voids. Where there is a void under the roof covering it shall comply with Section 504.2.1.1 or 504.2.1.2.

504.2.1.1 Airspace under roof covering. Where the roof covering is installed over a combustible deck and the roofing profile creates an airspace under the roof covering, the installation shall comply with the following:

1. Install a 72 lb. (32.7 kg) cap sheet complying with ASTM D3909 Standard Specification for “Asphalt Rolled Roofing (Glass Felt) Surfaced with Mineral Granules,” shall be installed over the roof deck.

Exception: Cap sheet is not required where no less than 1” of mineral wool board or other noncombustible material is located between the roofing material and wood framing or deck.

2. Bird stops shall be used at the eaves where the profile fits, to prevent the entry of debris at the eave.

3. Hip and ridge caps shall be mudded in to prevent intrusion of fire or embers.

504.2.1.2 Roof underlayment. A listed and labeled roof underlayment that has been tested as part of the roof assembly in accordance with ASTM E108 or UL 790 for Class A fire classification, installed in accordance with the underlayment manufacturer’s installation instructions and listing. Bird stops shall be used at the eaves when the profile fits, to prevent the entry of debris at the eave. Hip and ridge caps shall be mudded in to prevent intrusion of fire or embers.

Exception: Where the roof sheathing is fire-retardant-treated wood labeled for exterior use and complies with Section 2303.2 of the California Building Code, the underlayment shall not be required to comply with a Class A fire classification.

504.2.1 Roof covering voids. Where the roof covering is installed over a combustible deck and the roofing profile creates an airspace under the roof covering, the installation shall comply with Sections 504.2.1.1. through 504.2.1.3

504.2.1.1 Roof deck. The roof deck shall be provided with one of the following over the entire roof deck:

Exception: Roof decks with solid sheathing of fire-retardant-treated wood complying with Section 2303.2 of the California Building Code and labeled for exterior use.

      - Cap sheet complying with ASTM D3909.

      - A roof assembly that, when tested without the roof covering material, will pass the ASTM E108 or UL 790 Class C fire test.

      - A minimum thickness of 1 inch (25 mm) noncombustible mineral wool board or other noncombustible material between the roof covering and deck.

504.2.1.2 Eaves. Openings at the eaves shall be protected with fireblocking, or noncombustible birdstops, or eave closures to prevent the intrusion of fire or embers.

504.2.1.3 Ridges and hips. Openings at hip or ridge caps shall be mortared or otherwise protected with noncombustible material to prevent intrusion of fire or embers.

#### SUB-ITEM 4-5
Section 504.2.2 Roof valley flashings

[SFM proposal from the 2025 CWUI Work Group – Roofs Subgroup.]

504.2.2 Roof valleys flashings. Where roof valley flashing is provided, valley the flashings shall be not less than 0.019 inch (0.48 mm) (No. 26 galvanized sheet gauge) corrosion-resistant metal installed over one of the following with a minimum 36 inch (914 mm) width running the full length of the valley: a minimum 36-inch-wide (914 mm) underlayment consisting of one layer of 72-pound (32.4 kg) mineral-surfaced, nonperforated cap sheet complying with ASTM D3909 running the full length of the valley.

- A cap sheet complying with ASTM D3909.

- A Class A roofing assembly comprised of an underlayment and one layer of No. 26 galvanized sheet gauge flashing as the roof covering when tested in accordance with ASTM E108 or UL 790 and installed in accordance with the listing.

504.2.3 Flashing at intersections. Where the roof intersects with a wall, metal flashing or noncombustible material shall be applied vertically on the exterior of the wall in accordance with Section 504.5.1.

#### SUB-ITEM 4-6
Section 504.2.4 Skylights

[This proposed revision adds a pointer under the roof assembly section 504.2 for skylights.]

504.2.4 Skylights. Skylights, including tubular daylighting devices and sloped glazing shall comply with Section 504.8.

#### SUB-ITEM 4-7
Section 504.3.1 Protection of open eaves

[Proposed changes identified with gray highlight were included in the Emergency Regulations approved October 15, 2025. There are no additional changes proposed except for spelling correction in the word “Fascias”.]

504.3.1 Protection of open eaves. The exposed roof deck on the underside of unenclosed roof eaves shall consist of one or more of the following:

1. …

5. 2-inch (51 mm) nominal dimension lumber.

6. 5. One layer of 5/8-inch (16 mm) Type X gypsum sheathing applied behind an exterior covering on the underside of the roof deck.

7. 6. The exterior portion of a 1-hour fire-resistance-rated exterior assembly, as tested in accordance with ASTM E119 or UL 263, applied to the underside of the roof deck designed for exterior fire exposure, including assemblies using the gypsum panel and sheathing products listed in the Gypsum Association Fire Resistance Design Manual.

Fascias, if provided, shall be of fire-retardant-treated wood labeled for exterior use and complying with Section 2303.2 of the California Building Code, ignition-resistant building materials, materials approved for not less than 1-hour fire-resistance-rated construction or 2-inch (51 mm) nominal dimension lumber.

#### SUB-ITEM 4-8
Section 504.5 Exterior walls

[The Exterior wall sections are designed to work together, and compliance is achieved when the exterior wall complies with both the exterior wall construction provisions and the exterior wall covering provisions.]

504.5 Exterior walls. Exterior walls of buildings or structures shall be constructed with one or more of the following methods, unless they are covered  in accordance with Section 504.5.1 or provided with an exterior wall covering complying in accordance with Section 504.5.2 and 504.5.2.1.

- 1-hour fire-resistance-rated construction on the exterior side.

- Noncombustible materials.

- Heavy timber. Assembly of sawn lumber or glue-laminated wood with the smallest minimum nominal dimension of 4 inches (102 mm). Sawn or glue-laminated planks splined, tongue-and-grove or set close together and well spiked.

- Log wall construction.

- Wall assemblies that have been tested in accordance with the test procedures for a 10-minute direct flame contact exposure test set forth in ASTM E2707 with the conditions of acceptance shown in Section 504.9.3.

- Wall assemblies that meet the performance criteria in accordance with the test procedures for a 10-minute direct flame contact exposure test set forth in SFM Standard 12-7A-1.

- Wall assemblies suitable for exterior fire exposure containing one layer of 5/8-inch (15.9 mm) Type X gypsum sheathing applied behind the exterior wall covering or cladding on the exterior side of the framing.

- Wall assemblies suitable for exterior fire exposure with a 1-hour fire-resistance rating, rated from the exterior side, as tested in accordance with ASTM E119 or UL 263.

- Fire-retardant-treated wood labeled for exterior use and complying with Section 2303.2 of the California Building Code.

Such material shall extend from the top of the foundation to the underside of the roof sheathing

504.5.1 Exterior wall construction. Exterior walls of buildings or structures shall be constructed using one or more methods, as described below. Any exterior wall covering applied using these methods shall be in accordance with Section 504.5.2:

- 1-hour fire-resistance-rated construction with an exterior wall covering in accordance with Section 504.5.2.

- Ignition-resistant building materials in accordance with Section 503.2.

- Assembly of sawn lumber, cross-laminated timber or glue-laminated wood with the smallest minimum nominal dimension of 4 inches (102 mm). Sawn or glue-laminated planks shall be splined, tongue-and-grove or set close together and well spiked.

- Log wall construction.

- Wall assemblies that have been tested in accordance with the test procedures for a 10-minute direct flame contact exposure test set forth in ASTM E2707 with the conditions of acceptance shown in Section 504.9.3.

- Wall assemblies that meet the performance criteria in accordance with the test procedures for a 10-minute direct flame contact exposure test set forth in SFM Standard 12-7A-1.

Such material shall extend from the top of the foundation to the underside of the roof sheathing.

504.5.2 Exterior wall coverings. Exterior wall coverings shall comply with one or more of the following requirements:

- Noncombustible material.

- Ignition-resistant building material labeled for exterior use.

- Fire-retardant-treated wood labeled for exterior use and complying with the requirements of Section 2303.2 of the California Building Code.

- Fire-retardant-treated wood shingles and shakes which have been qualified in accordance with Section 1505.6 of the California Building Code for use as “Class B” roof covering shall be an acceptable alternative wall covering material where installed over solid sheathing.

Exception: Exterior wall coverings which are a component of an approved wall assembly complying with Section 504.5.

504.5.2.1 Extent of exterior wall covering. …

…

504.5.1 504.5.3 Flashing. A minimum of 6 inches (152 mm) of metal flashing or noncombustible material applied vertically on the exterior of the wall shall be installed at the ground, decking deck and roof intersections.

#### SUB-ITEM 4-9
Section 504.7.3.1 Deck Flashing

[SFM proposal from the 2025 CWUI Work Group – Roofs Subgroup.]

504.7.3.1 Deck Flashing. A minimum of a 6-inch (150 mm) metal flashing, applied vertically on the exterior of the wall, shall be installed at all deck-to-wall intersections. Flashing shall be applied vertically on the exterior of the wall where it intersects with a deck in accordance with Section 504.5.3.

#### SUB-ITEM 4-10
Section 504.8 Exterior glazing and subsections

[SFM proposal from the 2025 CWUI Work Group – Windows Subgroup.]

504.8 Exterior glazing. Exterior windows, window walls, and glazed doors, windows within exterior doors, and skylights shall be constructed of any of the following:

1.	Multilayered glazed panels with at least one pane of the inner pane of tempered glass and complying with Section 2406 of the California Building Code.

2.	Glass block units.

3.	Glazing with a fire-protection rating of not less than 20 minutes when tested without the hose stream test in accordance to NFPA 252, UL 10B, or UL 10C, or in accordance with NFPA 257 or UL 9.according to NFPA 257 or UL 9, and shall be exempt from the hose stream test.

4.	Glazing meeting the performance requirements of SFM Standard 12-7A-2.

5.	Skylights glazed with multilayered panels with at least one pane of tempered glass and complying with Section 2406 of the California Building Code.

504.8.1 Structural glass veneer. The wall assembly behind glass veneer shall comply with Section 504.5.

504.8.2 Operable skylights. The openings of operable Operable skylights shall be protected by noncombustible mesh screen and the dimension of the opening in the screen shall not exceed 1/8 inch (3.2 mm).

#### SUB-ITEM 4-11
Section 504.10 Vents

[SFM proposal from the 2025 CWUI Work Group – Vent Subgroup.]

504.10 Vents. Where provided, ventilation openings for enclosed attics, gable ends, ridge ends, under eaves and cornices, enclosed eave soffit spaces, enclosed rafter spaces formed where ceilings are applied directly to the underside of roof rafters, underfloor ventilation, foundations and crawl spaces, or any other opening intended to permit ventilation, either in a horizontal or vertical surface, shall be in accordance with Section 504.10.1 or Section 504.10.2 to resist building ignition from the intrusion of burning embers and flame through the ventilation openings. Ventilation openings for the following purposes shall comply with Section 504.10.1 or 504.10.2, as applicable:

- Openings into enclosed attics or enclosed rafter spaces in accordance with California Building Code Section 1202.2 or California Residential Code Section R806.

- Openings into under-floor areas in accordance with California Building Code Section 1202.4 or California Residential Code Section R408.2.

- Other ventilation openings for unoccupiable spaces, such as garages and mechanical equipment rooms.

Exception: Exhaust openings such as drain waste vents, dryer exhaust vents, kitchen exhaust vents, bathroom exhaust vents and direct vent appliances.

#### SUB-ITEM 4-12
Section 504.10.1 Vent testing

[SFM proposal from the 2025 CWUI Work Group – Vent Subgroup.]

504.10.1 Performance requirements Vent testing. Ventilation openings shall be fully covered with Wildfire Flame and Ember Resistant vents approved and listed by the California State Fire Marshal, or WUI vents tested in accordance with ASTM E2886, to demonstrate compliance with all the following requirements:

1. There shall be no flaming ignition of the cotton material during the Ember Intrusion Test of ASTM E2886.

2. The Flame Intrusion Tests of ASTM E2886 shall be conducted in both the horizontal and vertical orientations.

2.3. There shall be no flaming ignition during the Integrity Test portion of the Flame Intrusion Test.

4. The maximum temperature of the unexposed side of the vent shall not exceed 662°F (350°C).

#### SUB-ITEM 4-13
Sections 504.10.2 Roof ridge and off-ridge field vents and 504.10.3 Vent locations

[SFM proposal from the 2025 CWUI Work Group – Vent Subgroup.]

504.10.2 Off Roof ridge and off-ridge field vents. Vents Roof ridge and off-ridge field vents which are specifically excluded from the scope of ASTM E2886 that are installed on a sloped roof, such as dormer vents, shall comply with all of the following:

- Vents Ventilation openings shall be covered protected with a mesh material where the dimensions of the mesh therein shall be a minimum of 1/16 inch (1.6 mm) and shall not exceed ⅛ inch (3.2 mm) in diameter.

- The vent and mesh material shall be noncombustible.

- The vent and mesh material shall be corrosion resistant.

- Ventilation openings shall be located not less than 10 feet (3048 mm) from lot lines.

- The ventilation opening for off-ridge field vents shall not exceed 144 square inches (0.0929 m²) each.

504.10.3 Vent locations. Gable-end and dormer vents shall be located not less than 10 feet (3048 mm) from lot lines. Underfloor ventilation openings shall be located as close to grade as practical.

#### SUB-ITEM 4-14
Sections 504.11 Accessory Structures and subsections

[SFM proposal from the 2025 CWUI Work Group – Accessory Structures Subgroup.]

504.11 Accessory buildings and miscellaneous structures. Accessory buildings and miscellaneous structures that have the potential to pose a significant exterior fire exposure hazard during wildfires shall be constructed to conform to the ignition-resistance requirements of this section.

504.11.1 Applicability. Sections 504.11.2 through 504.11.36 apply to buildings accessory to an applicable building on the same lot and attached or detached miscellaneous structures that require a building permit, including but not limited to trellises, arbors, patio covers, gazebos and similar structures.

Exceptions:

- Decks shall comply with the requirements of Section 504.7.3.

- Awnings and canopies shall comply with the requirements of Section 3105 of the California Building Code.

504.11.2 Accessory structures greater than 120 sq ft Unless excluded in Section 501.1, accessory structures shall comply with Sections 504.2 through 504.10.

504.11.3 Accessory structures equal or less than 120 sq ft When required by the code official, accessory buildings 120 square feet (11.15 m²) or less and separated from an applicable building on the same lot by a distance of 3 feet (914.4 mm) or more but less than 30 feet (9144 mm) shall be constructed of noncombustible materials or of ignition-resistant building materials as described in Section 503.

504.11.2 Miscellaneous structures and accessory buildings within 3 feet. Miscellaneous structures that require a permit, and accessory buildings of any size, when separated from an applicable building on the same lot by a distance of less than 3 feet (914 mm), shall be constructed of noncombustible materials or ignition-resistant building materials as described in Section 503.2.4.

504.11.3 Accessory buildings greater than 120 square feet, located 3 feet or more but less than 50 feet. Accessory buildings that are greater than 120 square feet (11.15 m²) in size and separated from an applicable building on the same lot by a distance of 3 feet (914 mm) or more but less than 50 feet (15 240 mm) shall be constructed of noncombustible materials or of ignition-resistant building materials as described in Section 503.2.4.

504.11.4 Accessory buildings 120 square feet or less, located 3 feet or more but less than 50 feet. When required by the code official, accessory buildings 120 square feet (11.15 m²) or less and separated from an applicable building on the same lot by a distance of 3 feet (914 mm) or more but less than 50 feet (15 240 mm) shall be constructed of noncombustible materials or of ignition-resistant building materials as described in Section 503.2.4.

504.11.5 Miscellaneous structures located 3 feet or more but less than 50 feet. When required by the code official, miscellaneous structures that require a permit and are separated from an applicable building on the same lot by a distance of 3 feet (914 mm) or more but less than 50 feet (15 240 mm) shall be constructed of noncombustible materials or of ignition-resistant building materials as described in Section 503.2.4.

#### SUB-ITEM 4-15
Section 504.11.6 Roof construction

[SFM proposal from the 2025 CWUI Work Group – Roofs Subgroup.]

504.11.6 Roof construction. Roof assemblies and roof coverings of accessory buildings required to be constructed entirely of noncombustible materials or of ignition-resistant building materials shall comply with Sections 504.2 and 504.2.1. Roofs shall have a roofing assembly installed in accordance with its listing and the manufacturer’s installation instructions. Roof assemblies in Fire Hazard Severity Zones shall comply with a be classified as Class A fire classification when tested in accordance with ASTM E108 or UL 790.

#### SUB-ITEM 4-16
Section 507.1 General

[SFM proposal from the 2025 CWUI Work Group – Roofs Subgroup.]

507.1 General. The roof covering on buildings or structures in existence prior to the adoption of this code that are replaced or have 5050 percent or more replaced in a 12-month period shall be replaced with a roof covering required for new construction specified in Sections 504.2 and 504.2.1. All portions of a roof covering applied during an addition, alteration or repair to an existing structure shall meet at least a be classified as Class A fire classification when tested in accordance with ASTM E108 or UL 790.

#### Notation:

Authority: Health and Safety Code Sections 1250, 1502, 1568.02, 1569.70 - 1569.74, 1597.44 - 1597.65, 13108, 13108.5, 13114, 13143, 13143.2, 13143.6, 13145, 13146, 13211, 16022.5, 17921, 18928, 18949.2, 25500 through 25545; Government Code Sections 51176, 51177, 51178, 51179 and 51189; Public Education Code 17074.50; Public Resources Code Sections 4201 through 4204.

Reference(s): Health and Safety Code Sections 13108, 13108.5, 13113, 13113.5, 13114, 13132, 13132.7, 13133, 13135, 13143, 13143.1, 13143.2, 13143.6, 13143.9, 13145, 13146, 13210, 13211, 16022.5, 17921.

### ITEM 5
Chapter 6 Fire Protection Requirements

#### SUB-ITEM 5-1
User Note

[SFM proposal from the 2025 CWUI Work Group – Chapter 6 Subgroup.]

About this chapter: …

The requirements in this chapter reference the process for adoption of Very High Fire Hazard Severity Zones in the LRA; criteria for evaluating existing subdivisions that are at significant fire risk and are without an adequate secondary egress; and criteria for fire safety provisions required in the Safety Element of a city or county General Plan.

…

#### SUB-ITEM 5-2
Section 602.3.2 Final Fire Protection Plan

[SFM proposal from the 2025 CWUI Work Group – Chapter 6 Subgroup.]

602.3.2 Final fire protection plan. Final fire protection plan shall include items listed in Section 602.3.1 and the following:

  - A map identifying all proposed plants and existing vegetation proposed to remain in the fuel modification zones with a legend that includes a symbol for each proposed plant species. …

#### SUB-ITEM 5-3
Section 603.3.1 Contents

[SFM proposal from the 2025 CWUI Work Group – Chapter 6 Subgroup.]

603.3.1 Contents. Landscape plans shall contain the following:

    - Delineation of the 5-foot (1524 mm), 30-foot (9144 mm) and 100-foot (30 480 mm) fuel management zones from all structures.

    - …

#### SUB-ITEM 5-4
Sections 604.1 General and 604.3 Requirements

[SFM proposal from the 2025 CWUI Work Group – Chapter 6 Subgroup.]

604.1 General. Hazardous vVegetation and fuels shall be managed to reduce the severity of potential exterior wildfire exposure to buildings and to reduce the risk of fire spreading to buildings as required by applicable laws and regulations.

Defensible space shall be managed around all buildings and structures in State Responsibility Areas (SRA) as required in Public Resources Code 4291.

…

604.3 Requirements. Hazardous vVegetation and fuels around all buildings and structures shall be maintained, at a minimum, in accordance with the following laws and regulations:

      - Public Resources Code, Section 4291.

      - California Code of Regulations, Title 14, Division 1.5, Chapter 7, Subchapter 3, Article 3, Section 1299.03.

      - California Government Code, Section 51182.

      - California Code of Regulations, Title 19, Division 1, Chapter 7, Subchapter 1, Section 3.07.

#### Notation:

Authority: Health and Safety Code Sections 1250, 1502, 1568.02, 1569.70 - 1569.74, 1597.44 - 1597.65, 13108, 13108.5, 13114, 13143, 13143.2, 13143.6, 13145, 13146, 13211, 16022.5, 17921, 18928, 18949.2, 25500 through 25545; Government Code Sections 51176, 51177, 51178, 51179 and 51189; Public Education Code 17074.50; Public Resources Code Sections 4201 through 4204.

Reference(s): Health and Safety Code Sections 13108, 13108.5, 13113, 13113.5, 13114, 13132, 13132.7, 13133, 13135, 13143, 13143.1, 13143.2, 13143.6, 13143.9, 13145, 13146, 13210, 13211, 16022.5, 17921.

### ITEM 6
Chapter 7 Referenced Standards

#### SUB-ITEM 6-1
NFPA 1140

1140-2022	Standard for Wildland Fire Protection

101.6

#### Notation:

Authority: Health and Safety Code Sections 1250, 1502, 1568.02, 1569.70 - 1569.74, 1597.44 - 1597.65, 13108, 13108.5, 13114, 13143, 13143.2, 13143.6, 13145, 13146, 13211, 16022.5, 17921, 18928, 18949.2, 25500 through 25545; Government Code Sections 51176, 51177, 51178, 51179 and 51189; Public Education Code 17074.50; Public Resources Code Sections 4201 through 4204.

Reference(s): Health and Safety Code Sections 13108, 13108.5, 13113, 13113.5, 13114, 13132, 13132.7, 13133, 13135, 13143, 13143.1, 13143.2, 13143.6, 13143.9, 13145, 13146, 13210, 13211, 16022.5, 17921.

### ITEM 7
Appendix D Model Ordinance for Fire Hazard Severity Zone Adoption

[SFM proposes to adopt the Appendix D Model Ordinance for Fire Hazard Severity Zone Adoption. This requirement is driven by HSC Section 51179.]

#### Notation:

Authority: Health and Safety Code Sections 1250, 1502, 1568.02, 1569.70 - 1569.74, 1597.44 - 1597.65, 13108, 13108.5, 13114, 13143, 13143.2, 13143.6, 13145, 13146, 13211, 16022.5, 17921, 18928, 18949.2, 25500 through 25545; Government Code Sections 51176, 51177, 51178, 51179 and 51189; Public Education Code 17074.50; Public Resources Code Sections 4201 through 4204.

Reference(s): Health and Safety Code Sections 13108, 13108.5, 13113, 13113.5, 13114, 13132, 13132.7, 13133, 13135, 13143, 13143.1, 13143.2, 13143.6, 13143.9, 13145, 13146, 13210, 13211, 16022.5, 17921.