# FINAL EXPRESS TERMS
FOR PROPOSED BUILDING STANDARDS
OF THE DEPARTMENT OF HEALTH CARE ACCESS AND INFORMATION/
OFFICE OF STATEWIDE HOSPITAL PLANNING AND DEVELOPMENT
REGARDING THE 2025 CALIFORNIA MECHANICAL CODE,
CALIFORNIA CODE OF REGULATIONS, TITLE 24, PART 4
(OSHPD 05/25)

The state agency shall draft the regulations in plain, straightforward language, avoiding technical terms as much as possible and using a coherent and easily readable style. The agency shall draft the regulation in plain English. A notation shall follow the express terms of each regulation listing the specific statutes authorizing the adoption and listing specific statutes being implemented, interpreted, or made specific (Government Code Section 11346.2(a)(1)).

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic and ellipsis.

## LEGEND for EXPRESS TERMS (Based on model codes - Parts 2, 2.5, 3, 4, 5, 7, 9, 10)

- Model Code language appears upright

- Existing California amendments appear in italic

- Amended model code or new California amendments appear underlined & italic

- Repealed model code language appears upright and in strikeout

- Repealed California amendments appear in italic and strikeout

- Ellipses ( …) indicate existing text remains unchanged

## FINAL EXPRESS TERMS

### ITEM 1
Chapter 3 GENERAL REGULATIONS
Section 320.4 Telephone and Technology Equipment Centers.

320.4 Telephone and Technology Equipment Centers. [OSHPD 1, 2, & 4 & 5] Where telecommunications service entrance rooms, technology equipment centers, or technology distribution rooms are provided in accordance with Section 1224.5 or 1225.5.1.1 of the California Building Code, the following requirements shall apply:

320.4.1 Power for HVAC systems serving the room(s) shall be supplied by the Equipment Branch pursuant to the California Electrical Code. Where redundant systems are provided, only one shall be required to be supplied by the Equipment Branch.

320.4.2 Mechanical equipment or fixtures that are not directly related to the support of the room shall not be installed in or pass through the room.

Exception: Unrelated ductwork may be installed and shall be not less than 10 feet (3048 mm) above the finished floor.

320.4.3 HVAC systems shall be provided to maintain environmental conditions recommended in ASHRAE’s Thermal Guidelines for Data Processing Environment and the requirements of the specific equipment installed.

320.4.4 (Does not apply to OSHPD 2 or 5) Technology equipment centers shall have redundant cooling systems each of sufficient capacity to provide required cooling during periods of breakdown or maintenance of either system. One system shall be nonhydronic and on essential power.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Sections 129675-130079

### ITEM 2
Chapter 3 GENERAL REGULATIONS
Section 321 Essential Mechanical Provisions.

321.0 Essential Mechanical Provisions. [OSHPD 1, 2, 3 (Surgical Clinics only) 4 & 5] During periods of power outages essential electrical power shall be provided for the following equipment:

321.1 (Does not apply to OSHPD 3 surgical clinic.) All heating equipment and fans necessary to maintain a minimum temperature of 60°F (15.6°) in patient areas which are not specified in Section 322.0.

321.2 All heating equipment and fans necessary to maintain the minimum temperatures listed in Table 4-A for sensitive areas specified in Section 322.0.

321.3 (Does not apply to OSHPD 3 surgical clinic.) Cooling equipment necessary to maintain temperature and humidity listed in Table 4-A for a minimum of one operating room and other spaces as identified in the functional program.

321.4 Equipment necessary for humidification of the areas listed in Section 322.0.

321.5 All supply, return, and exhaust fans required to maintain the positive and negative air balances as required in Table 4-A.

321.6 All control components, control systems and fire and smoke dampers necessary for the normal operation of equipment required to have essential electrical power.

321.7 Alarms for airborne infection isolation rooms and protective environment rooms.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Sections 129675-130079

### ITEM 3
Chapter 4 VENTILATION AIR
Section 401.0 General, 402 Ventilation Air, 403 Ventilation Rates, 407 Ventilation System Details.

401.0 General.

401.1 Applicability. This chapter contains requirements for ventilation air supply, exhaust, and makeup air requirements for occupiable spaces within a building. [MOVE TO END][OSHPD 1, 1R, 2, 3, 4 & 5] See Sections 406.0 through 419.0. [SFM] Air filters shall comply with all requirements of Part 12, Title 24, Chapter 12-71, SFM Standard 12-71-1. Spaces within buildings, except those within a dwelling unit in residential occupancies where occupants are nontransient, shall comply with Section 402.0 through Section 404.0. Requirements for ventilation air rate for dwelling units in residential occupancies, where the occupants are nontransient, shall be in accordance with Section 405.0 or ASHRAE 62.2. [RELOCATE FROM ABOVE] [OSHPD 1, 1R, 2, 3, 4 & 5] See Sections 406.0 through 419.0.

402.0 Ventilation Air.

402.1 Occupiable Spaces. Occupiable spaces listed in Table 402.1 shall be designed to have ventilation (outdoor) air for occupants in accordance with this chapter. [DSA-SS] Ventilation air requirements for occupancies regulated by the California Energy Commission are found in the California Energy Code.

[CEC] Ventilation air requirements for occupancies regulated by the California Energy Commission and found in the California Energy Code supersede those of the California Mechanical Code.

[OSHPD 1, 2, 3, 4 & 5] Health care spaces shall meet the ventilation requirements found in Table 4-A. Ventilation rates for areas not specified in Table 4-A shall have minimum ventilation and air change rates per ANSI/ASHRAE Standard 62.1. Where areas with prescribed ventilation rates in both Standards 62.1 and Table 4-A exist, the higher of the two air change rates shall be used.

…

402.1.2 Ventilation in Health Care Facilities. Mechanical ventilation for health care facilities shall be designed and installed in accordance with this code, ASHRAE/ASHE 170, and NFPA 99. [OSHPD 1, 1R, 2, 3, 4 & 5] Ventilation for health care facilities shall be designed and installed in accordance with this code and Table 4-A or 4-C. Ventilation rates for areas not specified in Table 4-A or 4-C shall have minimum ventilation and air change rates per Section 403.0. Where areas with prescribed ventilation rates in both Section 403 and Table 4-A exist, the higher of the two air change rates shall be used. All supply-air, return air, and exhaust-air systems shall comply with this code and ASHRAE 170. When the requirements of this code conflict with ASHRAE 170, the most restrictive requirements shall prevail. The text of ASHRAE 170 shall be modified as follows:

…

(13) ASHRAE 170. Section 8.2 -- Modify as follows: Replace reference to Table 8-2 with reference to Table 4-A 4-C.

…

402.3 Mechanical Ventilation. [Not permitted for OSHPD 1, 2, 3, 4 & 5] Where natural ventilation is not permitted by this section or the California Building Standards Code, mechanical ventilation systems shall be designed, constructed, and installed to provide a method of supply air and either return air or exhaust air, or both, as applicable. Mechanical ventilation systems shall include controls, manual or automatic, that enable the fan system to operate wherever the spaces served are occupied. The system shall be designed to maintain minimum outdoor airflow as required by Section 403.0 under any load conditions.

402.4 Outdoor Air Intakes. Ventilation system outdoor air intakes shall be designed in accordance with Section 402.4.1 through Section 402.4.5. [ASHRAE 62.1:5.5] [OSHPD 1, 2, 3, 4 & 5] Healthcare facilities shall also comply with Section 407.2.1.

402.4.1 Location. Outdoor air intakes (including openings that are required as part of a natural ventilation system) shall be located such that the shortest distance from the intake to any specific potential outdoor contaminant source listed in Table 402.4.1 shall be equal to or greater than the following:

(1) The separation distance in Table 402.4.1 or

(2) The calculation methods in ASHRAE 62.1 Normative Appendix B and shall comply with all other requirements of this section. [ASHRAE 62.1:5.5.1]

…

403.0 Ventilation Rates. [Not permitted for OSHPD 1, 2, 3, 4 & 5 spaces listed in Table 4-A]

403.1 General. The design outdoor air intake flow rate for a ventilation system shall be determined in accordance with Section 403.2 through Section 403.10.

403.2 Zone Calculations. Ventilation zone parameters shall be determined in accordance with Section 403.2.1 through Section 403.2.3 for ventilation zones served by the ventilation system, except that the ventilation rates from ASHRAE/ASHE 170, shall be used for the occupancy categories, as applicable. [ASHRAE 62.1:6.2.1]

[OSHPD 1, 1R, 2, 3, 4 & 5] Ventilation rates for areas specified in Table 4-A shall comply with section 407.3.1.

403.2.1 Breathing Zone Outdoor Airflow. …

…

407.3 Air Balance.

407.3.1 The ventilation systems shall be designed and balanced to provide the general air balance relationship to adjacent areas, shown in Table 4-A. The ventilation systems shall be tested, adjusted, and balanced in accordance with Section 403.10 and the latest edition of standards published by the Associated Air Balance Council (AABC), the National Environmental Balancing Bureau (NEBB), or the Testing, Adjusting and Balancing Bureau (TABB). All testing and balancing shall be performed by a qualified independent agency certified by the AABC, NEBB, or TABB. Air balance tolerancing values shall not result in noncompliance of the minimum required pressurization per Table 4-A.

407.3.1.1 Clinic Spaces. Clinics compliant with California Building Code Sections 1226.6, 1226.10, 1226.11 and 1226.12 and licensed pursuant to Health and Safety Code Section 1204 shall have ventilation systems designed and balanced as shown in Table 4-C. Other licensed clinics shall be designed and balanced to provide the general air balance relationship to adjacent areas, shown in Table 4-A.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Sections 129675-130079

### ITEM 4
Chapter 4 VENTILATION AIR
Section 408.0 Filters, 415 Protective Environment Rooms.

408.2 Filters for Hospitals.

408.2.1 All air-ventilation systems shall comply with code requirements of this section and shall have filter bank efficiencies as listed in Table 4-B. The filtration level for each space shall meet the minimum level as indicated in Table 4-A.

408.3 Filters for Skilled Nursing Facilities, Intermediate Care Facilities, and Correctional Treatment Centers.

408.3.1 The air ventilation systems for skilled nursing facilities, intermediate care facilities and correctional treatment centers shall have filter bank efficiencies as listed in Table 4-CB. The filtration level for each space shall meet the minimum level as indicated in Table 4-A.

408.3.2…

408.4 Filters for Outpatient Facilities.

408.4.1 The air ventilation systems for outpatient facilities shall have filter bank efficiencies as listed in Table 4-B. The filtration level for each space shall meet the minimum level as indicated in Table 4-A or 4-C.

408.5 Filters for Recirculating Room Units.

408.5.1 Filters for recirculating room units shall comply with Section 407.4.5. Where Table 4-A does not permit air recirculated by means of room units, room units with a filtration level per Table 4-BA are permitted.

…

415.0 Protective Environment Rooms. [OSHPD 1, 2, 3, 4 & 5]

415.1 Air Distribution. The supply outlets and exhaust and return inlets shall be located to provide airflow patterns that prevent stagnation of the air and eliminate short circuiting of the supply to the exhaust or return. Supply air shall be delivered at or near the ceiling and near the patient's bed. HEPA filtration shall be provided in the air terminal device. All exhaust or return registers shall be located near the entrance to the protective environment room and not less than 3 inches (76 mm) nor more than 8 inches (203 mm) above the finished floor.

Exception: For correctional treatment centers, the location and design of the supply outlets and exhaust or return inlets shall not compromise the safety, security, and protection of staff, inmates and property.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Sections 129675-130079

### ITEM 5
Chapter 4 VENTILATION AIR
Table 4-A PRESSURE RELATIONSHIP AND VENTILATION REQUIREMENTS FOR GENERAL ACUTE CARE HOSPITALS, SKILLED NURSING FACILITIES, INTERMEDIATE CARE FACILITIES, OUTPATIENT FACILITIES, LICENSED CLINICS, CORRECTIONAL TREATMENT CENTERS, AND ACUTE PSYCHIATRIC HOSPITALS

| Function of Space (ee) | Pressure Relationship (d)(n) | Minimum Outdoor ach | Minimum Total ach | Exhausted Directly to Outdoors (j) | Recirculated Room Units (a) | Unoccupied Turndown | Filtration Level (r) | Design Relative Humidity (k), % | Design Temperature (l), °F/°C |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| NURSING UNITS AND OTHER PATIENT CARE AREAS |  |  |  |  |  |  |  |  |  |
| AII anteroom (1224.14.3.3) (u) | (e) | NR | 10 | Yes | No | No | B | NR | NR |
| AII room (1224.14.3) (u) | Negative | 2 | 12 | Yes | No | No | C | Max 60 | 70-75/21-24 |
| AII treatment/exam room (1224.4.4.1.3) | Negative | 2 | 12 | Yes | No | No | C | Max 60 | 70-75/21-24 |
| Cesarean Delivery room (1224.32.3.1.1) (m), (o) | Positive | 4 | 20 | NR | No | Yes | B | 20-60 | 68-75/20-24 |
| Delivery room (1224.32.3.2) (m), (o) | Positive | 4 | 20 | NR | No | Yes | B | 20-60 | 68-75/20-24 |
| Emergency department exam/treatment room (1224.33.3.6) (p) | NR | 2 | 6 | NR | NR | Yes (ff) | C | Max 60 | 70-75/21-24 |
| Emergency department human decontamination (1224.33) | Negative | 2 | 12 | Yes | No | No | C | NR | NR |
| Emergency department public waiting area (1224.33.3.5) | Negative | 2 | 12 | Yes (q) | NR | No | E | Max 65 | 70-75/21-24 |
| Emergency department trauma/resuscitation room (1224.33.3.7) (c) | Positive | 3 | 15 | NR | No | Yes | C | 20-60 | 70-75/21-24 |
| Emergency service triage area (1224.33.3.3) | Negative | 2 | 12 | Yes (q) | NR | No | E | Max 60 | 70-75/21-24 |
| Fast-track area (1224.33.4.2) | NR | 2 | 6 | NR | NR | Yes | E | NR | 70-75/21-24 |
| Infusion room (1224.39.4.2.3) | Positive | 2 | 6 | NR | NR | Yes | C | NR | 70-75/21-24 |
| Intensive care patient space (1224.29.1.2) (gg) | NR | 2 | 6 | NR | No | Yes | C | 30-60 | 70-75/21-24 |
| Intermediate care patient room (1224.38) (s) | NR | 2 | 6 | NR | NR | Yes | C | Max 60 | 70-75/21-24 |
| Labor/delivery/recovery (LDR) (1224.32.3.7) (s) | NR | 2 | 6 | NR | NR | Yes | C | Max 60 | 70-75/21-24 |
| Labor/delivery/recovery/postpartum (LDRP) (1224.32.3.7) (s) | NR | 2 | 6 | NR | NR | Yes | C | Max 60 | 70-75/21-24 |
| Lactation (1224.32.5.1.3) | NR | 2 | 6 | NR | NR | Yes | C | NR | 70-75/21-24 |
| Laser eye room (1224) | Positive | 3 | 15 | NR | No | Yes | C | 20-60 | 70-75/21-24 |
| Newborn intensive care (1224.29.2.6) | Positive | 2 | 6 | NR | No | Yes | C | 30-60 | 72-78/22-26 |
| Newborn intensive care formula room (1224.29.2.10) | Positive | 2 | 10 | NR | No | Yes | A | NR | 70-75/21-24 |
| Newborn/well baby nursery (1224.32.5) | NR | 2 | 6 | NR | No | Yes | C | 30-60 | 72-78/22-26 |
| Nourishment area or room (1224.4.4.5) | NR | NR | 2 | NR | NR | Yes | E | NR | NR |
| Nurse station (1224.4.4.2) (aa) | (aa) | (aa) | 2 | (aa) | (aa) | Yes | C | (aa) | (aa) |
| Nursery workroom (1224.32.5.1.4) | NR | 2 | 6 | NR | No | Yes | C | Max 60 | 72-78/22-26 |
| Observation (1224.33.5.1) | NR | 2 | 6 | NR | NR | Yes | C | NR | 70-75/21-24 |
| Operating room (1224.15.2.1) (m),(o) | Positive | 4 | 20 | NR | No | Yes | B | 20-60 | 68-75/20-24 |
| Operating/surgical cystoscopic rooms (1224.15.2.2.1) (m), (o) | Positive | 4 | 20 | NR | No | Yes | B | 20-60 | 68-75/20-24 |
| Patient care area corridor (1224.4.7) | NR | NR | 2 | NR | NR | Yes | C | NR | NR |
| Patient room (1224.14.1) | NR | 2 | 4 (y) | NR | NR | Yes | C | Max 60 | 70-75/21-24 |
| Patient bedroom, behavioral room (1224.30.1/1228.14.1) | NR | 2 | 2 | NR | NR | Yes | E | NR | NR |
| Patient holding preparation (1224.16.2) | NR | 2 | 6 | NR | No | Yes | C | NR | 70-75/21-24 |
| Patient toilet room (1224.4.4.8) | Negative | NR | 10 | Yes | No | Yes (ff) | E | NR | NR |
| Pediatric playroom (1224.30.3.1) | NR | 2 | 6 | NR | NR | Yes | C | NR | 70-75/21-24 |
| Post-anesthesia care unit and recovery (1224.16.3) | NR | 2 | 6 | NR Yes | No | Yes | C | 20-60 | 70-75/21-24 |
| Procedure room (1224.4.4.1.4) (o) | Positive | 3 | 15 | NR | No | Yes | C | 20-60 | 70-75/21-24 |
| Protective environment room (1224.14.4) (t) | Positive | 2 | 12 | NR | No | No | A | Max 60 | 70-75/21-24 |
| Protective environment anteroom (1224.14.4.3) (t) | (e) | NR | 10 | NR | No | No | A | NR | NR |
| Radiology waiting rooms (1224.18) | Negative | 2 | 12 | Yes (q),(w) | NR | Yes (ff) | E | Max 60 | 70-75/21-24 |
| Recreation/activity room (1224.31.1.11/1224.35.1) | NR | 2 | 6 | NR | NR | Yes | C | NR | 70-75/21-24 |
| Seclusion room (1224.4.4.1.5/1228.14.5) | NR | 2 | 6 | NR | NR | Yes | C | Max 60 | 70-75/21-24 |
| Semi-restricted corridor (1224.15.1) | NR | 2 | 4 | NR | NR | No | C | NR | NR |
| Sterile processing room (1224.15.3.3) | NR | 2 | 6 | NR | No | Yes | C | NR | NR |
| Treatment room (1224.4.4.1.2) (p) | NR | 2 | 6 | NR | NR | Yes | C | 20-60 | 70-75/21-24 |
| Waiting area primary care clinic [Relocated to Table 4-C] | Negative | 2 | 12 | Yes | No | Yes |  | NR | 70-75/21-24 |
| Wound intensive care (burn unit) (1224.29.1) | Positive | 2 | 6 | NR | No | Yes | A | 40-60 | 70-75/21-24 |
| DIAGNOSTIC AND TREATMENT |  |  |  |  |  |  |  |  |  |
| Bronchoscopy, sputum collection, and pentamidine administration (1224.39.3) (n), (x) | Negative | 2 | 12 | Yes | No | Yes | C | NR | 68-73/20-23 |
| Cancer treatment area (1224.39.4) | NR | 2 | 6 | NR | NR | Yes | E | Max 60 | 70- 75/21-24 |
| Class 1 imaging room (1224.18) | NR | 2 | 6 | NR | NR | Yes | C | Max 60 | 72- 78/22-26 |
| CT Scan (1224.18.3) | NR | 2 | 6 | NR | NR | Yes | C | Max 60 | 70-75/21-24 |
| Fluoroscopy room (1224.18.1) | Negative | 2 | 6 | Yes | No | Yes | C | NR Max 60 | 70-75/21-24 |
| MRI room (1224.18.4) | NR | 2 | 6 | NR | NR | Yes | C | NR Max 60 | 70-75/21-24 |
| Negative-pressure x-ray room | Negative | 2 | 12 | Yes | No | Yes | C | max 60 | 72-78/22-26 |
| Class 2 imaging room (1224.18.1/1224.28.4) (p) | Positive | 3 | 15 | NR | No | Yes | C | Max 60 | 70-75/21-24 |
| Angiography room (1224.18.2) | Positive | 3 | 15 | NR | No | Yes | C | max 60 | 70-75/21-24 |
| Cardiac catheterization lab (1224.28.2) | Positive | 3 | 15 | NR | No | Yes | C | max 60 | 70-75/21-24 |
| Electroconvulsive therapy procedure room (1224.28.6) | Positive | 3 | 15 | NR | No | Yes | C | 20-60 | 70-75/21-24 |
| Interventional imaging procedure room (1224.28.4) | Positive | 5 3 | 15 | NR | No | Yes | C | 20-60 | 70-75/21-24 |
| Class 3 imaging room (1224.28.5/1224.18.1) (m), (o) | Positive | 4 | 20 | NR | No | Yes | B | 20-60 | 68-75/21-24 |
| Hybrid operating room (1224.28.5) (m), (n), (o) | Positive | 4 | 20 | NR | No | Yes | B | 20-60 | 68-75/20-24 |
| Dental treatment (1226.6.1.3) [Relocated to Table 4-C] | NR | 2 | 3 | NR | NR | Yes |  | NR | 70–75/21–24 |
| Dialysis treatment area (1224.36.2.3) | NR | 2 | 6 | NR | NR | Yes | E | NR | 72-78/22-26 |
| Dialyzer reprocessing room (1224.36.2.12) | Negative | NR | 10(bb) | Yes | No | Yes (ff) | E | NR | NR |
| Gastrointestinal endoscopy procedure room (1224.39.3) (x) | NR | 2 | 6 | NR | No | Yes | C | 20-60 | 68-73/20-23 |
| General examination room (1224.4.4.1.1) | NR | 2 | 4 | NR | NR | Yes | E | Max 60 | 70-75/21-24 |
| Hydrotherapy (1224.35) | Negative | 2 | 6 | NR | NR | Yes | E | NR | 72-80/22-27 |
| Instrument processing room (1224.39.3.2) | Negative | 2 | 10 | Yes | No | No | C | NR | NR |
| Medication preparation room (1224.4.4.1) | NR | 2 | 4 | NR | NR | Yes | C | Max 60 | 70-75/21-24 |
| Nuclear medicine (Gamma, PET, SPECT) (1224.34.1.2) | Negative | 2 | 6 | Yes | No | No | C | NR | 70-75/21-24 |
| Nuclear medicine hot lab (1224.34.1.3) | Negative | NR | 6 | Yes | No | Yes (ff) | E | NR | 70-75/21-24 |
| Speech therapy room (1224.35.4) | NR | 2 | 2 | NR | NR | Yes | E | NR | 70–75/21–24 |
| Physical therapy (1224.35.2) | Negative | 2 | 6 | NR | NR | Yes | E | Max 65 | 72-80/22-27 |
| Occupational therapy (1224.35.3) | NR | 2 | 3 | NR | NR | Yes | E | NR | 70–75/21–24 |
| Special examination room (g) | NR | 2 | 6 | NR | NR | Yes | C | Max 60 | 70- 75/21-24 |
| Ultrasound (1224.18.5) | NR | 2 | 6 | NR | NR | Yes | C | Max 60 | 72-78/22-26 |
| SUPPORT SERVICES |  |  |  |  |  |  |  |  |  |
| Blood bank/tissue storage (1224.17.2.4) | NR | 2 | 6 | NR | NR | Yes | D | NR | NR |
| Blood draw/phlebotomy (1224.17.3) | NR | 2 | 6 | NR | NR | Yes | D | NR | 70-75/21-24 |
| Housekeeping (1224.4.15) | Negative | NR | 10 | Yes | No | No | E | NR | NR |
| Food and supply storage (1224.20.2.3) | NR | NR | 2 | NR | No | No | E | NR | 72-78/22-26 |
| Food preparation areas (1224.20.2.5) (i) | NR | 2 | 10 | NR | No | Yes | E | NR | 72-78/22-26 |
| Laboratory work area, bacteriology (1224.17.2) (f), (v) | Negative | 2 | 6 | Yes | NR | Yes | D | NR | 70-75/21-24 |
| Laboratory work area, biochemistry (1224.17.2) (f), (v) | Negative | 2 | 6 | Yes | NR | Yes | D | NR | 70- 75/21-24 |
| Laboratory work area, cytology (1224.17.2) (f),(v) | Negative | 2 | 6 | Yes | NR | Yes | D | NR | 70-75/21-24 |
| Laboratory work area, general (1224.17.2) (f), (v) | Negative | 2 | 6 | NR | NR | Yes | D | NR | 70- 75/21-24 |
| Laboratory work area, glasswashing (1224.17.2) (f) | Negative | 2 | 10 | Yes | NR | Yes | D | NR | NR |
| Laboratory work area, histology (1224.17.2) (f),(v) | Negative | 2 | 6 | Yes | NR | Yes | D | NR | 70- 75/21-24 |
| Laboratory work area, media transfer (1224.17.2) (f),(v) | Positive | 2 | 4 | NR | NR | Yes | D | NR | 70-75/21-24 |
| Laboratory work area, microbiology (1224.17.2) (f), (v) | Negative | 2 | 6 | Yes | NR | Yes | D | NR | 70-75/21-24 |
| Laboratory work area, nuclear medicine (1224.17.2) (f), (v) | Negative | 2 | 6 | Yes | NR | Yes | D | NR | 70-75/21-24 |
| Laboratory work area, pathology (1224.17.2) (f), (v) | Negative | 2 | 6 | Yes | NR | No | D | NR | 70–75/21–24 |
| Laboratory work area, serology (1224.17.2) (f), (v) | Negative | 2 | 6 | Yes | NR | Yes | D | NR | 70–75/21–24 |
| Laboratory work area, sterilizing (1224.17.2) (f) | Negative | 2 | 10 | Yes | NR | Yes | D | NR | 70–75/21–24 |
| Pharmacy Services: Pharmacy Areas (1224.19.2) (b) | Positive | 2 | 4 | NR | NR | Yes | C | Max 60 | 70–75/21–24 |
| Drug room (1224.19.1.2.1) | NR Positive | 2 | 4 | NR | NR | Yes | C | NR | 70–75/21–24 |
| HD ante room (1224.19.3.3.3) (b) | Positive | NR (dd) | 30 | NR | NR | NR | A | <60 | ≤68/≤20 |
| HD buffer room (1224.19.3.3.2) (b) | Negative | NR (dd) | 30 | Yes | No | NR | A | <60 | ≤68/≤20 |
| HD SCA (1224.19.3.3.4) (cc) | Negative | NR (dd) | 12 | Yes | NR | NR | E | NR | NR |
| HD storage (1224.19.3.3) (b) | Negative | NR (dd) | 12 | Yes | NR | NR | C | NR | NR |
| Non-HD ante room (1224.19.3.2.3) (b) | Positive | NR (dd) | 30 20 | NR | NR | NR | A | <60 | ≤68/≤20 |
| Non-HD buffer room (1224.19.3.2.2) (b) | Positive | NR (dd) | 30 | NR | No | NR | A | <60 | ≤68/≤20 |
| Non-HD SCA (1224.19.3.2.4) (dd) | NR | NR (dd) | NR | NR | NR | NR | E | NR | NR |
| Toilet room (1224.4.4.8) | Negative | NR | 10 | Yes | No | Yes | E | NR | 72–78/22–26 |
| Warewashing (1224.20.2.10) (r) | Negative | NR | 10 | Yes | No | Yes | E | NR | NR |
| SUPPORT SERVICES: STERILE PROCESSING |  |  |  |  |  |  |  |  |  |
| Clean assembly/workroom (1224.22.1) (z) | Positive | 2 | 4 | NR | No | No | C | Max 60 | 68–73/20–23 |
| Soiled workroom/decontamination room (1224.22.1) (z) | Negative | 2 | 6 | Yes | No | No | E | NR | 60–73/16–23 |
| Sterile storage room (clean/sterile medical/ surgical supplies) (1224.22.1) (z) | Positive | 2 | 4 | NR | NR | No | C | Max 60 | Max 75/24 |
| One-room sterile processing (1224.22) | NR | 2 | 6 | NR | No | No | C | NR | NR |
| Sterilizing equipment room | Negative | NR | 10 | Yes | NoNR | No | E | NR | NR |
| OTHER GENERAL SUPPORT SERVICES |  |  |  |  |  |  |  |  |  |
| Morgues and Autopsy room (1224.24) | Negative | 2 | 12 | Yes | No | No | E | NR | 68–75/20–24 |
| Clean linen storage room (1224.27 & 1224.14.2.9) | Positive | NR | 2 | NR | NR | Yes | C | NR | 72–78/22–26 |
| Hazardous material storage (1224.4.14) | Negative | 2 | 10 | Yes | No | No | E | NR | NR |
| Laundry, processing room (1224.27) | Negative | 2 | 10 | Yes | No | No | E | NR | NR |
| Linen and refuse chute room (1224.27 & 1224.4.14) | Negative | NR | 10 | Yes | No | No | E | NR | NR |
| Nonrefrigerated body holding room (1224.24) (h) | Negative | NR | 10 | Yes | No | No | E | NR | 70–75/21–24 |
| Regulated waste holding spaces (1224.4.14) | Negative | NR | 10 | Yes | No | No | E | NR | NR |
| Unsterile supply (1225.4.5.2.4) | NR | 2 | 2 | NR | NR | No | E | NR | NR |
| SUPPORT AREAS FOR NURSING UNITS AND OTHER PATIENT CARE AREAS |  |  |  |  |  |  |  |  |  |
| Clean supply room (1224.4.4.6.1) | Positive | NR | 2 | NR | NR | Yes | C | NR | NR |
| Clean utility/workroom (1224.4.4.6) | Positive | 2 | 4 | NR | NR | Yes | C | NR | NR |
| Soiled utility/workroom or soiled holding (1224.4.4.7) | Negative | 2 | 10 | Yes | No | No | E | NR | NR |
| BEHAVIORAL HEALTH |  |  |  |  |  |  |  |  |  |
| Patient bedroom, resident room (1228.14.1.2) | NR | 2 | 4 | NR | NR | Yes | E | NR | 70–75/21–24 |
| Seclusion room (1228.14.5) | NR | 2 | 4 | NR | NR | Yes | E | NR | 70–75/21–24 |
| Resident Group/multipurpose/activity/dining (1228.14.9) | NR | 2 | 4 | NR | NR | Yes | E | NR | 70–75/21–24 |
| SKILLED NURSING AND INTERMEDIATE CARE FACILITIES |  |  |  |  |  |  |  |  |  |
| AII room (1225.4.1.9) (bu) | Negative | 2 | 12 | Yes | No | Yes | D | Max 60 | 70-78/21-29 |
| AII anteroom (1225.4.1.9) (bu) | Negative | NR | 10 | Yes | No | Yes | D | Max 60 | 70-78/21-29 |
| Nurse station (aa) | (aa) | (aa) | 2 | (aa) | (aa) | (aa) | D | (aa) | (aa) |
| Resident living/activity/dining (1225.5.1.4/1225.5.2.5.1) | NR | 4 | 4 | NR | NR | Yes | D | Max 60 | 70-78/21-29 |
| Recreation/activity room (1225.5.1.4) | NR | 2 | 6 | NR | NR | Yes | D | NR | 70-75/21-24 |
| Resident room (1225.5.1.2.1/1225.5.2.3) | NR | 2 | 2 | NR | NR | Yes | D | Max 60 | 70-78/21-29 |
| Resident corridor (1225.5.1.1) | NR | NR | 4 | NR | NR | Yes | D | NR | 70-78/21-29 |
| Special purpose room (1225.4.1.8) | NR | 2 | 6 | Yes | NR | Yes | D | Max 60 | 70-75/21-24 |
| Shower room (1224.14.2.14) | Negative | NR | 10 | Yes | No | No | D | NR | 70-75/21-24 |
| Toilet/bathing room (1225.4.1.6) | Negative | NR | 10 | Yes | No | No | D | NR | 70-78/21-29 |
| SERVICE |  |  |  |  |  |  |  |  |  |
| Clean linen storage (1225.4.5.2.1) | Positive | NR | 2 | NR | NR | No | D | NR | 72-78/22-26 |
| Dietary storage (1225.4.2.2.10) | NR | NR | 2 | NR | No | No | E | NR | 72-78/22-26 |
| Food preparation center (1225.4.2.2.3) (i) | NR | 2 | 10 | NR | No | Yes | E | NR | 72-78/22-26 |
| Hair salon (1225.6) | Negative | NR | 10 | Yes | NR | Yes | E | NR | 70-78/21-29 |
| Laundry, central and personal (1225.4.7/1225.5.2.5.7) | Negative | 2 | 10 | Yes | No | No | E | NR | NR |
| Linen and trash chute room (1225.4.7) | Negative | NR | 10 | Yes | No | No | E | NR | NR |
| Medication preparation room (1225.4.1.1.1) | NR | 2 | 4 | NR | NR | Yes | D | Max 60 | 70-75/21-24 |
| Soiled linen sorting and storage (1225.4.7) | Negative | NR | 10 | Yes | No | No | E | NR | NR |
| Unsterile supply (1225.4.5.2.4) | NR | 2 | 2 | NR | NR | No | E | NR | NR |
| Warewashing (1225.4.2.2.7) | Negative | NR | 10 | Yes | No | Yes | E | NR | NR |
| SUPPORT SPACE |  |  |  |  |  |  |  |  |  |
| Clean utility room (1225.4.1.3.1) | Positive | 2 | 4 | NR | NR | No | D | NR | NR |
| Hazardous waste storage (1225) | Negative | 2 | 10 | Yes | No | No | E | NR | NR |
| Housekeeping room (1225.4.6) (j) | Negative | NR | 10 | Yes | NR | No | E | NR | NR |
| Soiled utility/workroom or soiled holding (1225.4.1.3.2) | Negative | 2 | 10 | Yes | No | No | E | NR | NR |

…

b. Additional air change, ISO class, continuous pressure monitoring and filtering requirements for compounding areas shall comply with California Board of Pharmacy regulations Title 16 §17356 & §175137, and USP <797> & <800>. …

…

r. Exhaust rate shall meet or exceed local requirements. Table entries are the minimum filter levels required for the space. Refer to Table 4-B for filtration level requirements. Operating rooms and Class 3 imaging rooms listed in Table 4-B for special procedures shall provide filtration level A with HEPA filtration.

…

dd. The requirements for the non-HD segregated compounding area shall meet the minimum requirements for the room which it is located. Outside air change rates for compounding spaces shall comply with Section 403.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Sections 129675-130079

### ITEM 6
Chapter 4 VENTILATION AIR
Table 4-B.

TABLE 4-B
FILTER EFFICIENCIES FOR CENTRAL VENTILATION AND AIR-CONDITIONING SYSTEMS IN GENERAL ACUTE CARE HOSPITALS, SKILLED NURSING FACILITIES, INTERMEDIATE CARE FACILITIES, OUTPATIENT FACILITIES, LICENSED CLINICS, CORRECTIONAL TREATMENT CENTERS AND ACUTE PSYCHIATRIC HOSPITALS 1 [OSHPD 1, 2, 3, 4 & 5]

[Due to accessibility requirements, the columns and headers in the amended ASHRAE table are changed from their original format. Once the rulemaking is approved and codified, the published table will reflect the ASHRAE format.]

| Filtration Level | AREA DESIGNATION | MINIMUM NUMBER OF FILTER BANKS | NO. 11 Filter Efficiency % Filter Location | NO. 11 (Minimum Efficiency Reporting Value MERV)56 | NO. 21 Filter Efficiency % Filter Location | NO. 21 (Minimum Efficiency Reporting Value MERV)56 | A.T.D.2 Filter Efficiency % Filter Location | A.T.D.2 (Minimum Efficiency Reporting Value MERV)56 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A | Operating room or Class 3 imaging room designated for Oorthopedic procedures operating room, bone marrow transplant operating room, organ transplant operating room, neurosurgery or dedicated burn unit procedures. NICU formula preparation room, NICU treatment area/room, protective environment rooms5 | 3 | 30% | (8) | 90% | (14) | 99.97%4 | HEPA3 |
|  | Protective environment rooms | 3 | 30% | (8) | 90% | (14) | 99.97%4 | HEPA3 |
| B | Operating room, operating/surgical cystoscopic room, cesarean operating room, class 3 imaging, hybrid operating room | 2 | 30% | (8) | 95% | (16) | — | — |
| C | Angiography; cardiac catheterization labs class 1 and 2 imaging; interventional imaging procedure rooms; delivery rooms, nurseries; patient care, treatment, exam, cystoscopy, diagnostic, and related areas; airborne infection isolation rooms; areas providing direct patient service or clean supplies such as sterile and clean processes, and patient area corridors | 2 | 30% | (8) | 90% | (14) | — | — |
| D | Laboratories, all areas for skilled nursing inpatient care, treatment and/or diagnosis, and those areas providing direct service or cleaning supplies | 2 | 30% | (8) | 80% | (13) |  |  |
| E | Outpatient, Aadministrative, med staff support areas, bulk storage, soiled holding areas, food preparation areas, public cafeterias, and laundries, psychiatric hospitals intended for the care and treatment of inpatients who do not require acute medical services | 17 | 80% | (13) | — | — | — | — |
|  | Psychiatric hospitals intended for the care and treatment of inpatients who do not require acute medical services | 17 | 80% | (13) | — | — | — | — |

…

4 HEPA filters shall be located in the air terminal device of the room served.

5 HEPA filters shall be located in the air terminal device of the room served. HEPA filters shall be permitted to be located in the air handling unit subject to the exception in ASHRAE 170, Section 7.2.2(c). HEPA filter installation shall be designed and equipped to permit safe removal, disposal and replacement of filters.

6 …

7…

8 Filters are not required for evaporative coolers serving laundries.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Sections 129675-130079

### ITEM 7
Chapter 4 VENTILATION AIR
TABLE 4-C PRESSURE RELATIONSHIP AND VENTILATION REQUIREMENTS FOR LICENSED CLINICS

TABLE 4-C 
FILTER EFFICIENCIES FOR CENTRAL VENTILATION AND AIR-CONDITIONING SYSTEMS IN SKILLED NURSING FACILITIES, INTERMEDIATE CARE FACILITIES AND CORRECTIONAL TREATMENT CENTERS1 [OSHPD 2 & 4]

1 Based on ASHRAE 52.2.

2 Filters are not required for evaporative coolers serving laundries.

3 The numbers in parentheses represent MERV rating based on ASHRAE 52.2.

4 Additional prefilters with a minimum efficiency of MERV 8 may be used to reduce maintenance for filters.

TABLE 4-C
PRESSURE RELATIONSHIP AND VENTILATION REQUIREMENTS FOR LICENSED CLINICS [OSHPD 3]

[Due to accessibility requirements, the headers in the amended ASHRAE table are changed from their original format. Once the rulemaking is approved and codified, the published table will reflect the ASHRAE format.]

| Function of Space (b) (f) | Pressure Relationship (d) (n) | ach Design Option Minimum Outdoor ach (q) | ach Design Option Minimum Total ach (q) | Exhausted Directly to Outdoors (j) | Recirculated Room Units (a) | Unoccupied Turndown | Filter Level (c) | Design Relative Humidity (i), % | Design Temperature °F/°C (k) | Rp-Ra Air-Class Design Option Air Class (q) | Rp-Ra Air-Class Design Option Rp cfm/person Min. Space Pop. (q) | Rp-Ra Air-Class Design Option Ra cfm/ft (q) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL DIAGNOSTIC AND TREATMENT |  |  |  |  |  |  |  |  |  |  |  |  |
| Birthing room (1226.11.1.1) | NR | 2 | 3 | NR (h) | NR | Yes | C | Max 60 | 70-75/21-24 | 2 | 10 / 4 | 0.18 |
| Clinic urgent exam/treatment (1226.6.1) (e) | NR | 2 | 3 | NR | NR | Yes | E | NR | 70-75/21-24 | 2 | 7.5 / 3 | 0.12 |
| Urgent care treatment (e) | NR | 2 | 3 | NR | NR | Yes |  | NR | 70-75/21-24 | 2 | 7.5 / 3 | 0.12 |
| Urgent care triage | NR | 2 | 3 | NR | NR | Yes |  | NR | 70-75/21-24 | 2 | 7.5 / 3 | 0.12 |
| Clinic observation (1226.6) | NR | 2 | 2 | NR | NR | Yes | E | NR | 70-75/21-24 | 2 | 7.5 / 3 | 0.12 |
| Waiting area primary care clinic (1226.6.5.1.2) (g) | Negative | 2 | 12 | Yes | No | Yes | E | NR | 70-75/21-24 | 3 | - | - |
| General examination room (1226.4.1.1) | NR | 2 | 2 | NR | NR | Yes | E | NR | 70-75/21-24 | 1 | 7.5 / 3 | 0.12 |
| Laboratory work room (1226.4.2.4) (l) | NR | 2 | 3 | NR (h) | NR | Yes | E | NR | 70-75/21-24 | 2 | 7.5 / 3 | 0.12 |
| Medication room (1226.6.2.2) | NR | 2 | 2 | NR | NR | Yes | E | Max 60 | 70-75/21-24 | 1 | 5 / 2 | 0.18 |
| Class 1 Imaging rooms (1226.6) (g) | NR | 2 | 3 | NR | NR | Yes | E | Max 60 | 72-78/22-26 | 1 | 7.5 / 3 | 0.12 |
| Psychiatric examination room (1226.12) | NR | 2 | 3 | NR | NR | Yes | E | NR | 70-75/21-24 | 1 | 5 / 2 | 0.06 |
| Psychiatric consultation room (1226.12) | NR | 2 | 3 | NR | NR | Yes | E | NR | 70-75/21-24 | 1 | 5 / 2 | 0.06 |
| Psychiatric group room (1226.12) | NR | 2 | 3 | NR | NR | Yes | E | NR | 70-75/21-24 | 1 | 5 / 2 | 0.06 |
| Psychiatric seclusion room (1226.12) | NR | 2 | 2 | NR | NR | Yes | E | NR | 70-75/21-24 | 2 | 10 / 3 | 0.12 |
| ECT procedure room | NR | 2 | 3 | NR | NR | Yes |  | NR | 70-75/21-24 | 1 | 7.5 / 3 | 0.12 |
| Physical therapy individual room (1226.10.5.1) | NR | 2 | 3 | NR (h) | NR | Yes | E | NR | 70-75/21-24 | 2 | 10 / 3 | 0.12 |
| Physical therapy exercise area (1226.10.5.3) | NR | 2 | 3 | NR (h) | NR | Yes | E | NR | 70-75/21-24 | 2 | 10 / 3 | 0.18 |
| Hydrotherapy (1226.10.5) | Negative | 2 | 3 | Yes | NR | Yes | E | NR | 72-80/22-27 | 3 | 20 / 2 | 0.12 |
| Physical therapeutic pool (1226.10.5) | Negative | 2 | 10 | Yes | NR | Yes | E | NR | 72-80/22-27 | 3 | -- | 0.48 |
| Speech therapy room (1226.10.7) | NR | 2 | 2 | NR | NR | Yes | E | NR | 70-75/21-24 | 1 | 5 / 2 | 0.06 |
| Occupational therapy (1226.10.6) | NR | 2 | 3 | NR | NR | Yes | E | NR | 70-75/21-24 | 1 | 5 / 2 | 0.06 |
| Prosthetics and orthotics room (1226.10) | NR | 2 | 3 | NR | NR | Yes | E | NR | 70-75/21-24 | 2 | 10 / 3 | 0.18 |
| Dental treatment (1226.6.7) (e) | NR | 2 | 3 | NR | NR | Yes | E | NR | 70-75/21-24 | 1 | 10 / 3 | 0.18 |
| Other dental treatment areas (1226.6.7.2) (e) | NR | 2 | 3 | NR | NR | Yes | E | NR | 70-75/21-24 | 1 | 5 / 2 | 0.06 |
| Toilet room (1226.9.4.1) | Negative | NR | 4 (r) | Yes | No | No | E | NR | NR | 3 | -- | -- |
| SERVICE /SUPPORT SPACE |  |  |  |  |  |  |  |  |  |  |  |  |
| Environmental services Housekeeping room (1226.4.11) | Negative | NR | 6 | Yes | No | No | E | NR | NR | 3 | -- | -- |
| Clean supply holding (1226.4.13.3) (m) (n) | NR | 2 | 2 | NR | NR | Yes | E | NR | NR | 1 | 5 / 2 | 0.12 |
| Soiled holding (1226.4.13.4) (m) (o) (p) | Negative | NR | 6 | Yes | No | No | E | NR | NR | 3 | 5 / 2 | 0.12 |

Table 4-C is based on ASHRAE Standard 170-2021, “Ventilation of Healthcare Facilities,” Table 8-2 with amendments, and it is used with expressed written permission from ASHRAE. Copyright notice for ASHRAE Standards ©ASHRAE, www.ashrae.org. 2021 ASHRAE Standard-170.

a. Except where indicated by a “No” in this column, recirculating room HVAC units (with heating or cooling coils) are acceptable for providing that portion of the minimum total air changes per hour that is permitted by Section 8.2(a)(5) 407.4.5. Because of the cleaning difficulty and potential for buildup of contamination, recirculating room units shall not be used in areas marked “No.”

b. Examination rooms (identified as “specialty infection control [IC] exam rooms”) programmed for use by patients with undiagnosed gastrointestinal symptoms, undiagnosed respiratory symptoms, or undiagnosed skin symptoms. Functions not specifically identified in this table shall be in accordance with the ventilation requirements found in Table 4-A.

c. Table entries are the minimum filter efficiencies required for the space. Refer to Section 6.4 Table 4-B of this document for further clarification of filtration requirements. The minimum efficiency reporting value (MERV) is based on the method of testing described in ASHRAE Standard 52.2 (Informative Note: ASHRAE [2012] in Informative Appendix E).

d. Pressure monitoring devices are not required for any spaces indicated in Table 8-2. Simple visual methods such as ball-in-tube or flutterstrip are suggested should pressurization verification of air-flow direction be desired or required by others. Provide approximately 10% differential cfm between supply and return/exhaust airflow but not less than 25 cfm differential shall be provided regardless of room size. Room function, size, and tightness may be considered when determining the differential airflow required. Where continuous directional control is not required, variations between supply cfm and return or exhaust cfm shall be minimized in accordance with Section 407.4.2.

e. Treatment rooms used for procedures with nitrous oxide shall contain provisions for exhausting anesthetic waste gases, and the minimum total air changes shall be increased to 6. When this condition occurs the Rp-Ra air-class design option cannot be used.

f. Informative Note: Parenthetic notations following a space name are paragraph references to the relevant FGI Guidelines (FGI 2018a, 2018b, 2018c) in Informative Appendix E California Building Code sections from Chapter 12. These paragraph references are provided to the user to aid in the application of design requirements.

g. Refer to Table 8-1 under the space type “Diagnostic imaging waiting” for space ventilation requirements in an instance where a facility proposes an imaging waiting area and their ICRA determines that the imaging waiting area requires special consideration to reduce the risk of airborne infection transmission. The requirement that all room air be exhausted directly to outdoors applies only to waiting rooms programmed to hold patients who are waiting for diagnosis of respiratory disease. Other waiting room ventilation requirements may comply with Section 403.

h. In some areas with potential contamination and/or odor concerns, exhaust air shall be discharged to the outdoors and not recirculated to other areas.

i. The relative humidity (RH) ranges listed are the minimum and/or maximum allowable at any point within the design temperature range required for that space.

j. Unless otherwise noted in (h) above, the exhaust rate shall meet or exceed minimum total air change requirement. Where the “exhaust directly to Outdoors” column is marked yes, all exhaust air shall be discharged directly to the outdoors and not recirculated to other areas. Recirculation room units may be provided where the column is marked yes provided air is not recirculated to other areas. To satisfy exhaust needs, constant replacement air from the outdoors is necessary when the system is in operation.

k. Systems shall be capable of maintaining the rooms within the range during normal operation. Lower or higher temperature shall be permitted when patients’ comfort and/or medical conditions require those conditions.

l. This room is intended for basic blood and urine specimen testing and short-term storage only. Outpatient facilities that provide the following specialized service spaces/rooms should consult Table 7-1 4-A for ventilation requirements: laboratory work areas, including the specialty lab services such as bacteriology, biochemistry, cytology, glasswashing, histology, media transfer, microbiology, nuclear medicine, pathology, serology, and/or sterilizing.

m. Outpatient facilities that provide the following specialized service spaces/rooms should consult Table 8-1 4-A for ventilation requirements: laundry, general, and soiled linen sorting and storage.

n. Refer to Table 8-1 4-A under the space type “Clean utility/workroom or clean supply” for space ventilation requirements if a clean workroom space is provided.

o. Refer to Table 8-1 4-A under the space type “Soiled utility/workroom or soiled holding” for space ventilation requirements if a soiled workroom space is provided.

p. This space is permitted to include hazardous material storage (general medical waste). If actual regulated waste holding is anticipated, refer to Table 8-1 4-A under the space type “Regulated waste holding” for ventilation requirements.

q. See Section 8.2(a)(6) and 8.2(a)(8). For ventilation systems using the air class design option the requirements of Section 403 shall be met. The design zone population (Pz) shall equal the largest (peak) number of people expected to occupy the room/space during typical use. For Multiple-Zone Recirculating Systems and Variable air Volume systems the minimum primary airflow (Vpz-min) for each zone shall be determined by the equation Vpz-min = Voz × 1.5.

r. Toilet exhaust shall not be less than 70cfm/water closet.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Sections 129675-130079

### ITEM 8
Chapter 5 EXHAUST SYSTEMS
Section 505.0 Product-Conveying Systems.

…
505.0 Product-Conveying Systems.
…
505.12 Pharmacies – Compounding Area of Parenteral Solutions. [CA – Board of Pharmacy]…
…
507.7 505.13 Pharmaceutical Hazardous Drug (HD) Compounding Exhaust Discharge. [OSHPD 1, 2, 3, 4 & 5] Exhaust discharge from fans serving the HD compounding suite shall extend at least 710 feet (21343048 mm) above the roof and discharge vertically upward. Self-draining stacks or equivalent shall be used for rain protection. Rain caps which divert the exhaust toward the roof shall be prohibited.

…

Part II - Commercial Hoods and Kitchen Ventilation.
507.0 General Requirements.
…
507.7 Pharmaceutical Compounding Exhaust Discharge… [Relocate to 505.13]

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Sections 129675-130079

### ITEM 9
Chapter 6 DUCT SYSTEMS
Section 602.0 Material.

602.0 Material.
602.1 General. Materials used for duct systems shall comply with Section 602.2 through Section 602.6 as applicable.

Exception: [OSHPD 1, 1R, 2, 3, 4 & 5] See Section 407.4.2.

[Not permitted for OSHPD 1, 1R, 2, 3, 4 & 5] Concealed building spaces or independent construction within buildings shall be permitted to be used as ducts or plenums. Gypsum board shall not be used for positive pressure ducts.

Exception: In healthcare facilities, concealed spaces shall not be permitted to be used as ducts or plenums. [OSHPD 1, 1R, 2, 3, 4 & 5] See Section 407.4.3.

#### Notation:

Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Sections 129675-130079