# COMMISSION ACTION MATRIX – 45-DAY
HEALTH FACILITIES (HF) CODE ADVISORY COMMITTEE

## 2025 CALIFORNIA BUILDING CODE, TITLE 24, PART 2 VOL. 1
AGENCY: OFFICE OF STATEWIDE HOSPITAL PLANNING AND DEVELOPMENT, OSHPD 02/25

### LEGEND:

CAC Actions: Approve, Disapprove, Approve as Amended, Further Study Required

Agency Responses: Accept, Disagree, Withdraw

CBSC Actions: Approve, Disapprove, Approve as Amended, Further Study Required

Matrix Paper Color (for commission action only): GREEN = uncontested items, YELLOW = challenged items, SALMON = withdrawn, no action required

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic and ellipsis.

- Model Code language appears upright

- Existing California amendments appear in italic

- Amended model code or new California amendments appear underlined & italic

- Repealed model code language appears upright and in strikeout

- Repealed California amendments appear in italic and strikeout

- Ellipses (…) indicate existing text remains unchanged

### ITEM 1
Chapter 12, INTERIOR ENVIRONMENT, Section 1224 HOSPITALS [OSHPD 1]

Amend sections listed below.

| OSHPD 02/25 ITEM 1 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 1-1 | Table 1224.4.6.1 Station outlets for oxygen. | Approve as Amended | Disagree |  | Amendment to add a row for infant resuscitation space in LDRP room distinguishing it from the same space in a cesarean delivery room; revise the required number of OB recovery room vacuum inlets; revise the required number of cardiac catheterization lab medical air inlets; and revise footnote 3. CAC: Approve as Amended under criteria #6, recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended. |  |
| - 1-2 | Table 1224.4.6.5 Location of nurse call devices. Footnote 1. | Approve as Amended | Disagree |  | Amendment to add Alternative Birthing Clinics (ABCs) to the exception in footnote 1. CAC: Approve as Amended under criteria #6, recommendation to capitalize “clinics” for consistency. POST CAC: The word “clinics” was removed to align with sentence structure. |  |
| - 1-3 | Table 1224.4.6.5 Location of nurse call devices. Footnote 2. | Approve as Amended | Disagree |  | Amendment to add a new footnote 2 allowing Alternative Birthing Clinics (ABCs) to use an alternative nurse call system. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-4 | Table 1224.4.6.5 Location of nurse call devices. Footnote 3. | Approve as Amended | Disagree |  | Amendment to add a new footnote 3 allowing nurse call devices to be located in the MRI control room. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-5 | 1224.4.11.2.2 Wet cleaning. | Approve as Amended | Disagree |  | Amendment to require integral coved wall base at permanently installed casework in wet cleaning rooms and to add room types to the required areas. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-6 | Table 1224.4.19 Sound transmission limitations in hospitals. Footnote 1. | Approve as Amended | Disagree |  | Amendment to correct reference standard number in table footnote 1. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-7 | 1224.16.2.3 Handwashing stations. | Approve as Amended | Disagree |  | Amendment to add language stating that handwashing stations shall be uniformly distributed. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-8 | 1224.18.3.1 Spaces required. | Approve as Amended | Disagree |  | Amendment to remove “if provided”. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-9 | 1224.19.1.1 Licensed pharmacy. | Approve as Amended | Accept |  | Amendment to change specific Title 16 reference to general reference in the Note. CAC: Approve as Amended under criteria #6, recommendation to review the use of the term “California Pharmacy Law”. POST CAC: Document names confirmed with Board of Pharmacy and amendment revised. |  |
| - 1-10 | 1224.19.2.1.3 Non-sterile compounding areas. | Approve as Amended | Disagree |  | Amendment changing terms to match terms used in Title 16. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-11 | 1224.19.3.1 General. through 1224.19.3.2.2.1 Air quality. | Approve as amended | Disagree |  | Amendments renumbering references to align with renumbering in Title 16. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-12 | 1224.19.3.2.2.5 Pass-throughs cabinets. | Approve as Amended | Disagree |  | Amendment to revise section title. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-13 | 1224.19.3.2.3.2 Air quality through 1224.19.3.3.4 Hazardous segregated compounding area | Approve as Amended | Accept |  | Amendments renumbering references to align with renumbering in Title 16. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: The word “anteroom” was changed to “anterooms”. |  |
| - 1-14 | 1224.20.2.8 Dining area. | Approve as Amended | Disagree |  | Amendment to correct spelling. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-15 | 1224.22.1 Minimum requirements. | Approve as Amended | Disagree |  | Amendment to add requirements for the type and locations of sinks in a Central Sterile Supply space in alignment with the requirements of the California Plumbing Code. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-16 | 1224.29.1.15 Support. | Further Study Required | Disagree |  | Amendment to add a note to item 6 clarifying the purpose of gurney and wheelchair storage in NICU. CAC: Further Study Required under criteria #8, recommendation to move “gurney and wheelchair storage” into the language of the requirements as opposed to the section title, and to remove “note” from the language if the intent is to have regulatory effect. POST CAC: “Note” was removed. “Gurney and wheelchair storage” was retained as the section title to maintain consistency with the rest of the sections’ format and was not proposed as new or repealed language. |  |
| - 1-17 | 1224.32.3.8.2.11 Housekeeping room. | Approve as Amended | Disagree |  | Amendment to add a pointer to the location of housekeeping room requirements. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-18 | 1224.33.2.1 Exterior entrance. | Approve as Amended | Accept |  | Amendment to revise the language describing the requirements for Emergency Medical Service area entrances. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. Recommendation to add “Standby” to “Emergency Medical Service area”, and “as” before “required”. POST CAC: ET revised as recommended. |  |
| - 1-19 | 1224.35.1 Rehabilitation center space. | Further Study Required | Disagree |  | Amendment to add requirements for rehabilitation center space including exit doors with panic hardware, door width for wheelchair patients, grab bars in toilet rooms, and patient training bathtubs. CAC: Further Study Required under criteria #6 and #8, recommendations to clarify the meaning of “group activity area”; coordinate the panic hardware requirement language with similar requirements for egress; remove “i.e.” from the language for specificity; and clarify where the 44” door width applies. POST CAC: Some but not all of the recommendations were addressed in the revised ET. See ISOR for explanation. |  |
| - 1-20 | 1224.35.2 Physical therapy service space. | Approve as Amended | Disagree |  | Amendment to add a requirement for grab bars in patient toilet rooms. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-21 | 1224.35.3 Occupational therapy service space. | Approve as Amended | Accept |  | Amendment to add requirements for minimum area dimensions, privacy screens, and grab bars. CAC: Approve as Amended under criteria #6. CAC recommended moving item #6 into item #5. POST CAC: ET revised as recommended. |  |
| - 1-22 | 1224.36.2.3 Individual patient treatment areas. | Approve as Amended | Accept |  | Amendment to add language clarifying the required clearances in treatment areas. CAC: Approve as Amended under criteria #6. CAC recommended changing the “4-foot” to “4 feet” and making grammatical changes. POST CAC: ET revised as recommended. |  |
| - 1-23 | 1224.36.3.2 Patient storage. | Approve as Amended | Disagree |  | Amendment to add language clarifying that storage is required when outpatient dialysis is provided. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-24 | 1224.36.3.3 Waiting room. | Approve as Amended | Disagree |  | Amendment to add an exception where a waiting room is not required. CAC: Approve as Amended under criteria #6, general recommendation to make grammatical changes throughout Item 1 proposals. POST CAC: No change in ET, no change was recommended |  |
| - 1-25 | 1224.39.4.2.3 Individual patient treatment areas. | Approve as Amended | Accept |  | Amendment to add language clarifying the required clearances in treatment areas. CAC: Approve as Amended under criteria #6. CAC recommended changing the “4-foot” to “4 feet” and making grammatical changes. POST CAC: ET revised as recommended. |  |

### ITEM 2
Chapter 12, INTERIOR ENVIRONMENT, Section 1225 SKILLED NURSING AND INTERMEDIATE CARE FACILITIES [OSHPD 2]

Amend sections listed below.

| OSHPD 02/25 ITEM 2 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 2-1 | 1225.4.1.7 Patient/nurse call system. | Approve | Accept |  | Amendment to change pointer from indicating requirements in California Electrical Code to California Building Code. |  |
| - 2-2 | 1225.1.1 General construction. through 1225.1.1.1.2 Technology distribution room. | Approve | Accept |  | Amendment to change requirements for communication systems in skilled nursing and intermediate-care facilities, adding Sections 1225.5.1.1.1 Communications systems. through 1225.5.1.1.1.2 technology distribution room. |  |
| - 2-3 | 1225.5.1.4.1 Skilled nursing facilities. | Further Study Required | Disagree |  | Amendment to add a requirement for outdoor space at skilled nursing facilities. CAC: Further Study Required under criteria #6, recommendation to clarify the requirements of “outdoor space” and make proposed language more precise. POST CAC: Licensing and reference documents only require that a space is provided with no additional specific requirements. “Shall be provided” has been added to the proposed language for clarity. |  |
| - 2-4 | 1225.6.6 SPECIAL TREATMENT PROGRAM SERVICE. | Approve | Accept |  | Amendment to change language to align with language in Title 22. |  |

### ITEM 3
Chapter 12, INTERIOR ENVIRONMENT, Section 1226 CLINICS [OSHPD 3]

Amend sections listed below.

| OSHPD 02/25 ITEM 3 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 3-1 | 1226.1 Scope. | Approve | Accept |  | Amendment to remove specific clinic types from scoping language. |  |
| - 3-2 | 1226.2 Application. | Approve | Accept |  | Amendment to clarify the pointer to other Parts of Title 24 are specific to the OSHPD 3 provisions of those regulations, and remove reference to the specific clinic types in Section 1226.1. |  |
| - 3-3 | 1226.2.1 Outpatient clinical services. | Approve | Accept |  | Amendment to remove existing language and move information to Sections 1226.4 and 1226.6. |  |
| - 3-4 | 1226.2.2 Special services. | Approve | Accept |  | Amendment to move this section to be under section for outpatient clinical services of a hospital. |  |
| - 3-5 | 1226.52.1 OUTPATIENT CLINICAL SERVICES OF A HOSPITAL. | Approve | Accept |  | Amendment to renumber existing scoping language Section 1226.5 to this Section and add language clarifying that these clinics are licensed by the California Department of Public Health (CDPH). |  |
| - 3-6 | 1226.2.1.1 Cardiac catheterization laboratory services. | Approve | Accept |  | Amendment to rename and renumber from 1226.2.2. |  |
| - 3-7 | 1226.4 General Construction. | Approve | Accept |  | Amendment to state that general construction requirements apply to all the clinic types listed in 1226 except as modified in each specific clinic type. |  |
| - 3-8 | 1226.4.1 Examination and treatment areas, when required. and 1226.4.2 Miscellaneous requirements, when required. | Approve | Accept |  | Amendment to add “when required” to these section titles. |  |
| - 3-9 | 1226.4.3 Corridors. | Approve as Amended | Accept |  | Amendment to clarify that one or more of the corridor options may be required. CAC: Approve as Amended under criteria #8, recommendation to coordinate charging language better with subsections by removing “width” from charging language, as not all subsections are strictly about width. POST CAC: ET revised as recommended. |  |
| - 3-10 | 1226.4.3.5 Contiguous functions. | Approve | Accept |  | Amendment to repeal the first sentence, add new language to reflect the intent and support the exceptions, and clarify a term used in Exception 1. |  |
| - 3-11 | 1226.4.4.1 Patient Ttoilet room doors. | Approve | Accept |  | Amendment to add “patient” to the title and add language to the section to clarify that the requirement is only for patient toilet room doors, not all toilet room doors. |  |
| - 3-12 | 1226.4.8.2 Dimensions. | Approve as Amended | Withdraw |  | Amendment to revise the language to reflect that requirements apply to at least one elevator in a clinic where the services that would have patients transported in wheeled stretchers. CAC: Approve as Amended under criteria #6, recommendation to clarify the scope of this requirement and make clear which clinics must comply, as whether patients will be transported in wheeled stretchers may be ambiguous. POST CAC: Withdraw the proposal as current code language is adequate. |  |
| - 3-13 | 1226.4.9 Garbage, solid waste, medical waste and trash storage. | Approve | Accept |  | Amendment to correct grammar. |  |
| - 3-14 | 1226.4.10, 1226.4.12, and 1226.4.13 | Approve | Disagree |  | Amendment to add “when provided” to these section titles. POST CAC: Grammatical changes made. |  |
| - 3-15 | 1226.4.13.2 Medication station. | Approve | Accept |  | Amendment to correct grammar and add “or area”. |  |
| - 3-16 | 1226.4.13.2.1 Medication preparation room or area. | Approve | Accept |  | Amendment to repeal Item 2, “sink”. |  |
| - 3-17 | 1226.4.13.4 Soiled workroom or soiled holding room. | Approve | Accept |  | Amendment to revise Item 1 and the body of the text to use the term “clinical sink”. |  |
| - 3-18 | 1226.4.13.5, 1226.4.13.6, and 1226.4.13.7 | Approve | Accept |  | Amendment to add “when provided” or “when required” to these section titles and remove it from the language of the sections. |  |
| - 3-19 | 1226.4.14.1 Patient toilet room(s). | Approve | Accept |  | Amendment to repeal “primary Care” from the exception and allow the exception to apply to all clinics. |  |
| - 3-20 | 1226.4.14.2 Specimen and/or blood collection facilities, when required. | Approve | Accept |  | Amendment to add “when required” to the section title and remove “when provided” from the language of the section. |  |
| - 3-21 | 1226.4.17.3 Staff lounge, when required. | Approve | Accept |  | Amendment to add “when required” to the section title and remove “when provided” from the language of the section. |  |
| - 3-22 | OUTPATIENT CLINICAL SERVICES OF A HOSPITAL | Approve | Accept |  | Amendment to repeal section title because it is repetitive of the section title in 1226.5. |  |
| - 3-23 | 1226.5 SERVICE SPACES, WHEN PROVIDED, FOR OUTPATIENT CLINICAL SERVICES OF A HOSPITAL. | Approve | Accept |  | The existing scoping language is moved to Section 1226.2.1. Amendment to add new title, add clarifying language, and a sentence to point the code reader to the general construction requirements. |  |
| - 3-24 | GENERAL SUPPORT AREAS FOR OUTPATIENT CLINICAL SERVICES - | Approve | Accept |  | Amendment to repeal section title because it is repetitive of the section title in 1226.5. |  |
| - 3-25 | 1226.5.1.2 Specimen and/or blood collection facilities. | Approve | Accept |  | Amendment to correct reference section number. |  |
| - 3-26 | 1226.5.11, 1226.5.12, 1226.5.13, and 1226.5.14 | Approve | Accept |  | Amendment to remove “when provided” from the language of these sections. |  |
| - 3-27 | 1226.6 PRIMARY CARE CLINICS. | Approve | Accept |  | Amendment to add that primary care clinics are licensed by CDPH pursuant to HSC Section 1204 (a) to the charging language in this section. |  |
| - 3-28 | 1226.6.1.2 Treatment room(s), when provided. | Approve | Accept |  | Amendment to add “when provided” to the title of the section and remove it from the middle of the first sentence. |  |
| - 3-29 | 1226.6.1.3 Dental examination and treatment areas. through 1226.6.1.3.4 Imaging.; 1226.6.1.4 Oral surgery.; and 1226.6.2.5 Consultation room. | Approve | Accept |  | Amendment to renumber these sections to 1226.6.7 and appropriate subsection numbers. |  |
| - 3-30 | 1226.6.2.6 Sterilization facilities, when provided. | Approve as Amended | Accept |  | Amendment to add “when provided” to the section title. CAC: Approve as Amended under criteria #8, recommendation to remove the redundant “when provided” from the language of the requirements, as this is now in the section title. POST CAC: ET revised as recommended. |  |
| - 3-31 | 1226.6.2.7 Laboratory. | Approve | Accept |  | Amendment to renumber this section to an appropriate subsection in Section 1226.6.7. |  |
| - 3-32 | 1226.6.3.2 Specimen collection and/or blood collection facilities. | Approve | Accept |  | Amendment to correct reference section number. |  |
| - 3-33 | 1226.6.5.1.2 Outpatient waiting room. | Approve | Accept |  | Amendment to add more specificity while still referencing Section 1224.4.5. |  |
| - 3-34 | 1226.6.5.1.3 Public toilet(s). | Approve | Accept |  | Amendment to add a pointer to the California Plumbing Code. |  |
| - 3-35 | 1226.6.5.1.4 Public telephone access. | Further Study Required | Withdraw |  | Amendment to clarify the telephone requirement stating that a telecommunication device shall be readily accessible. CAC: Further Study Required under criteria #3, #6, and #7, recommendation to clarify the term “telecommunication device” for access requirements associated with it and ensure that requirements are similar to those for the term “telephone”. POST CAC: Withdraw the proposal as further defining the requirements may cause more confusion than clarification. |  |
| - 3-36 | 1226.6.5.1.5 Drinking fountain(s). | Approve | Accept |  | Amendment to clarify the drinking water requirement by revising the section title and language. |  |
| - 3-37 | 1226.6.7 Dental examination and treatment areas. through 1226.6.7.8 Sterilization facilities. | Approve | Accept |  | Amendment to renumbered sections related to dental examination and treatment areas consolidating them under Section 1226.6.7. Add new section about sterilization facilities. |  |
| - 3-38 | SPECIALTY CLINICS. | Approve | Disagree |  | Amendment to add a new header and new charging language to clarify that specialty clinics are licensed by CDPH pursuant to HSC Section 1204 (b). POST CAC: Correction made to referenced code sections. |  |
| - 3-39 | SURGICAL CLINICS | Approve | Accept |  | Amendment to add a new header so the code user can way-find that Surgical Clinics are listed. |  |
| - 3-40 | 1226.8.5.1.2 Outpatient waiting room. | Approve | Accept |  | Amendment to add more specificity while still referencing Section 1224.4.5. |  |
| - 3-41 | 1226.8.5.1.3 Public toilet(s). | Approve | Accept |  | Amendment to add a pointer to the California Plumbing Code. |  |
| - 3-42 | 1226.8.5.1.4 Public telephone access. | Further Study Required | Withdraw |  | Amendment to clarify the telephone requirement stating that a telecommunication device shall be readily accessible. CAC: Further Study Required under criteria #3, #6, and #7, recommendation to clarify the term “telecommunication device” for access requirements associated with it and ensure that requirements are similar to those for the term “telephone”. POST CAC: Withdraw the proposal as further defining the requirements may cause more confusion than clarification. |  |
| - 3-43 | 1226.8.5.1.5 Drinking fountain(s). | Further Study Required | Disagree |  | Amendment to clarify the drinking water requirement by revising the section title and language. CAC: Further Study Required under criteria #3, #6, and #7, recommendation to clarify accessibility requirements associated with the language “drinking water shall be readily accessible”. POST CAC: No changes in ET. See ISOR for explanation. |  |
| - 3-44 | 1226.9.1.3 Individual patient treatment areas. | Approve as Amended | Accept |  | Amendment to add language clarifying the required clearances in treatment areas. CAC: Approve as Amended under criteria #6, recommendation to revise unit of measurement grammar. POST CAC: ET revised as recommended. The word “foot” was revised to “feet”. |  |
| - 3-45 | 1226.9.4.3 Specimen collection facilities. | Approve | Accept |  | Amendment to correct reference section number. |  |
| - 3-46 | 1226.10.1.1 Patient toilet room(s). | Approve | Accept |  | Amendment to add language detailing requirements for patient toilet rooms including requiring grab bars and to remove the pointer to Section 1226.4.14.1. |  |
| - 3-47 | 1226.10.3.1.2 Outpatient waiting room. | Approve | Accept |  | Amendment to add more specificity while still referencing Section 1224.4.5. |  |
| - 3-48 | 1226.10.3.1.3 Toilets. | Approve | Accept |  | Amendment to add a pointer to the California Plumbing Code. |  |
| - 3-49 | 1226.10.3.1.4 Drinking fountain(s). | Further Study Required | Disagree |  | Amendment to clarify the drinking water requirement by revising the section title and language. CAC: Further Study Required under criteria #3, #6, and #7, recommendation to clarify accessibility requirements associated with the language “drinking water shall be readily accessible”. POST CAC: No changes in ET. See ISOR for explanation. |  |
| - 3-50 | 1226.10.3.1.5 Telephone. | Further Study Required | Withdraw |  | Amendment to clarify the telephone requirement stating that a telecommunication device shall be readily accessible. CAC: Further Study Required under criteria #3, #6, and #7, recommendation to clarify the term “telecommunication device” for access requirements associated with it and ensure that requirements are similar to those for the term “telephone”. POST CAC: Withdraw the proposal as further defining the requirements may cause more confusion than clarification. |  |
| - 3-51 | 1226.12 PSYCHOLOGY CLINICS. | Approve | Accept |  | Amendment to add a sentence to clarify that these types of clinics are licensed by CDPH pursuant to HSC 1204.1. |  |
| - 3-52 | 1226.12.1.1.2 Outpatient waiting room. | Approve | Accept |  | Amendment to add more specificity while still referencing Section 1224.4.5. |  |
| - 3-53 | 1226.12.1.1.3 Public toilet(s). | Approve | Accept |  | Amendment to add a pointer to the California Plumbing Code. |  |
| - 3-54 | 1226.12.1.1.4 Drinking fountain(s). | Further Study Required | Disagree |  | Amendment to clarify the drinking water requirement by revising the section title and language. CAC: Further Study Required under criteria #3, #6, and #7, recommendation to clarify accessibility requirements associated with the language "drinking water shall be readily accessible”. POST CAC: No changes in ET. See ISOR for explanation. |  |
| - 3-55 | 1226.12.1.1.5 Public telephone. | Further Study Required | Withdraw |  | Amendment to clarify the telephone requirement stating that a telecommunication device shall be readily accessible. CAC: Further Study Required under criteria #3, #6, and #7, recommendation to clarify the term “telecommunication device” for access requirements associated with it and ensure that requirements are similar to those for the term “telephone”. POST CAC: Withdraw the proposal as further defining the requirements may cause more confusion than clarification. |  |

### ITEM 4
Chapter 12, INTERIOR ENVIRONMENT, Section 1226.11 ALTERNATIVE BIRTHING CLINICS [OSHPD 3]

Amend sections listed below.

| OSHPD 02/25 ITEM 4 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 4-1 | 1226.11 ALTERNATIVE BIRTHING CLINICS. | Approve as Amended | Accept |  | Amendment to add the facility type “primary care clinics” to the scope of this section and language to provide additional clarification about the types of facilities licensed by the California Department of Public Health to which this section would apply. CAC: Approve as Amended under criteria #8, recommendation to revise “centers” to “clinics” for consistency with terms throughout the code. POST CAC: ET revised as recommended. |  |
| - 4-2 | 1226.11.1.1 Birthing room. | Approve | Accept |  | Amendment to revise (reduce) the required dimensions for birthing room size. |  |
| - 4-3 | 1226.11.1.3 Nurse call system. Exception | Approve | Accept |  | Amendment to add an exception that allows alternative birthing clinics with three or fewer birthing rooms to use an alternative nurse call system as approved by CDPH. |  |
| - 4-4 | 1226.11.1.6 Window. | Approve | Accept |  | Amendment to change the requirement for an outside window in the birthing rooms to be optional. |  |
| - 4-5 | 1226.11.1.8 Reserved Newborn care area. | Approve | Accept |  | Amendment to repeal this section. |  |
| - 4-6 | 1226.11.1.9 Examination room. | Approve | Accept |  | Amendment to revise the pointer to Section 1224.4.4.1.1. and add a sentence to clarify that a birthing room may be used as an examination room. |  |
| - 4-7 | 1226.11.2.5 Crash Emergency cart space. | Approve | Accept |  | Amendment to change the terminology from crash cart to emergency cart. |  |
| - 4-8 | 1226.11.2.6 Reserved Clean-up room. | Approve | Accept |  | Amendment to repeal this section. |  |
| - 4-9 | 1226.11.3 Reserved. Support areas for mother and newborn | Approve | Accept |  | Amendment to repeal this section heading. |  |
| - 4-10 | 1226.11.2.103.1 Patient toilet room(s). | Approve | Accept |  | Amendment to renumber this section from 1226.11.3.1 to 1226.11.2.10 and to remove the nurse call requirement in patient toilet rooms. |  |
| - 4-11 | 1226.11.5.1.2 Outpatient waiting room. | Approve | Accept |  | Amendment to add more specificity while still referencing Section 1224.4.5. |  |
| - 4-12 | 1226.11.5.1.3 Public toilet(s). | Approve | Accept |  | Amendment to add a pointer to the California Plumbing Code. |  |
| - 4-13 | 1226.11.5.1.4 Public telephone. | Further Study Required | Withdraw |  | Amendment to clarify the telephone requirement stating that a telecommunication device shall be readily accessible. CAC: Further Study Required under criteria #3, #6, and #7, recommendation to clarify the term “telecommunication device” for access requirements associated with it and ensure that requirements are similar to those for the term “telephone”. POST CAC: Withdraw the proposal as further defining the requirements may cause more confusion than clarification. |  |
| - 4-14 | 1226.11.5.1.5 Drinking fountain(s). | Further Study Required | Disagree |  | Amendment to clarify the drinking water requirement by revising the section title and language. CAC: Further Study Required under criteria #3, #6, and #7, recommendation to clarify accessibility requirements associated with the language "drinking water shall be readily accessible”. POST CAC: No changes in ET. See ISOR for explanation. |  |
| - 4-15 | 1226.11.6.3 Staff lounge. | Further Study Required | Withdraw |  | Amendment to state the requirements for a staff lounge and remove the pointer to requirements in Section 1226.4.17.3. CAC: Further Study Required under criteria #3, #6, and #7, recommendation to clarify “adequate” and make the requirement less vague. POST CAC: Withdraw the proposal as defining “adequate” may constitute a material changing of the code requirement. |  |

### ITEM 5
Chapter 12, INTERIOR ENVIRONMENT, Section 1228 ACUTE PSYCHIATRIC HOSPITALS [OSHPD 5]

Amend sections listed below.

| OSHPD 02/25 ITEM 5 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 5-1 | 1228.13.1.1 Indoor activity rooms. and 1228.20.1 Dining area. | Approve | Accept |  | Amendment to change all uses of the term “room” to “area” in these sections to clarify the space requirements that meet the intended function of the space. |  |