# 45-DAY EXPRESS TERMS
FOR PROPOSED BUILDING STANDARDS
OF THE DEPARTMENT OF HEALTH CARE ACCESS AND INFORMATION/
OFFICE OF STATEWIDE HOSPITAL PLANNING AND DEVELOPMENT
REGARDING THE 2025 CALIFORNIA EXISTING BUILDING CODE,
CALIFORNIA CODE OF REGULATIONS, TITLE 24, PART 10
(OSHPD 07/25)

The state agency shall draft the regulations in plain, straightforward language, avoiding technical terms as much as possible and using a coherent and easily readable style. The agency shall draft the regulation in plain English. A notation shall follow the express terms of each regulation listing the specific statutes authorizing the adoption and listing specific statutes being implemented, interpreted, or made specific (Government Code Section 11346.2(a)(1)).

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic and ellipsis.

## LEGEND for EXPRESS TERMS (Based on model codes - Parts 2, 2.5, 3, 4, 5, 7, 9, 10)

- Model Code language appears upright

- Existing California amendments appear in italic

- Amended model code or new California amendments appear underlined & italic

- Repealed model code language appears upright and in strikeout

- Repealed California amendments appear in italic and strikeout

- Ellipses ( …) indicate existing text remains unchanged

## 45-DAY EXPRESS TERMS

### ITEM 1
CHAPTER 3A PROVISION FOR ALL COMPLIANCE METHODS

…

#### SECTION 304A—STRUCTURAL DESIGN LOADS AND EVALUATION AND DESIGN PROCEDURES

304A.3.5 Modifications to ASCE 41-13 for SPC-2 and SPC-4D. The text of ASCE 41-13 shall be modified as indicated in Sections 304A.3.5.1 through 304A.3.5.1718.

304A.3.5.13 ASCE 41-13 Section 10.7.1.1. Modify ASCE 41-13 Section 10.7.1.1 with the following:

Monolithic Reinforced Concrete Shear Walls and Wall Segments. For nonlinear procedures, shear walls or wall segments with axial loads greater than 0.35 Po shall be included in the model as primary elements with appropriate strength and stiffness degrading properties assigned to those components subject to the approval of the enforcement agent. For linear procedures, the effects of deformation compatibility shall be investigated using moment-curvature section analyses and cyclic testing results of similar components to determine whether strengthening is necessary to maintain the gravity load-carrying capacity of that component.

Horizontal wall segments or spandrels reinforced similar to vertical wall segments or piers shall be classified as wall segments, not shear wall coupling beams, in Tables 10-19 through 10-22. Horizontal wall segments or spandrels controlled by shear action and reinforced similar to vertical wall segments or piers shall be classified as wall segments, not shear wall coupling beams, in ASCE 41-13 Table 10-20 and Table 10-22.

Exception: Shear-controlled horizontal wall segments or spandrels with either closed hoops or stirrups anchored to the longitudinal reinforcing at the top and bottom with a standard hook may be classified as a shear wall coupling beam.

…

304A.3.5.15 ASCE 41-13 Section 11.1. Modify ASCE 41-13 Section 11.1 by the following:

Scope: ...

304A.3.5.16 ASCE 41-13 Chapter 13.

Penthouse Structures: Penthouse structures with aggregate area that is less than one-third of the roof area and are not an extension of the building frame may be evaluated using either criteria 1 or 2 listed below:

- ASCE 41-13 Chapter 13 criteria under BSE-1E. The connection to the existing structure shall be designed for amplified omega level (Ω=2) demands.

- ASCE 41-13 Chapter 13 criteria under BSE-2E.

All other penthouse structures shall be evaluated using their respective material chapter for both BSE-1E and BSE-2E against Damage Control and Collapse Prevention respectively.

304A.3.5.1617 ASCE 41-13 Section 14.1. Modify ASCE 41-13 Section 14.1 by the following:

Scope: For buildings located in Seismic Design Category F, verification of the interstory lateral displacements, the strength adequacy of the seismic force-resisting system and anchorage to the foundation shall be accomplished using the Nonlinear Dynamic Procedure.

304A.3.5.1718 ASCE 41-13 Chapter 15 and 16. Not permitted by OSHPD.

…

304A.3.6 Modifications to ASCE 41-23. The text of ASCE 41-23 shall be modified as indicated in Sections 304A.3.6.1 through 304A.3.6.910.

...

304A.3.6.8 ASCE 41-23 Section 11.1. Modify ASCE 41-23 Section 11.1 by the following:

Scope: Unreinforced masonry walls (including unreinforced infill walls) and partitions are not permitted for General Acute Care (GAC) hospital buildings.

304A.3.6.9 ASCE 41-23 Chapter 13.

Penthouse Structures: Penthouse structures with aggregate area that is less than one-third of the roof area and are not an extension of the building frame may be evaluated using either criteria 1 or 2 listed below:

- ASCE 41-23 Chapter 13 criteria under BSE-1E. The connection to the existing structure shall be designed for amplified omega level (Ω=2) demands.

- ASCE 41-23 Chapter 13 criteria under BSE-2E.

All other penthouse structures shall be evaluated using their respective material chapter for both BSE-1E and BSE-2E against Damage Control and Collapse Prevention respectively.

304A.3.6.910 ASCE 41-23 Chapter 16 and 17. Not permitted by OSHPD.

…

#### Notation:

Authority: Authority: Health and Safety Code, Sections 1275, 18942, 129850

Reference(s): Health and Safety Code, Sections 129675-130079