# COMMISSION ACTION MATRIX – 45 day
GREEN Building – PLUMBING, ELECTRICAL, MECHANICAL & ENERGY AD-HOC (GREEN/PEME) CODE ADVISORY COMMITTEE

## 2025 California mechanical code, TITLE 24, PART 4 
AGENCY: office of statewide hospital planning and development, OSHPD 05/25

### LEGEND:

CAC Actions: Approve, Disapprove, Approve as Amended, Further Study Required

Agency Responses: Accept, Disagree, Withdraw

CBSC Actions: Approve, Disapprove, Approve as Amended, Further Study Required

Matrix Paper Color (for commission action only): GREEN = uncontested items, YELLOW = challenged items, SALMON = withdrawn, no action required

If using assistive technology, please adjust your settings to recognize underline, strikeout, italic and ellipsis.

- Model Code language appears upright

- Existing California amendments appear in italic

- Amended model code or new California amendments appear underlined & italic

- Repealed model code language appears upright and in strikeout

- Repealed California amendments appear in italic and strikeout

- Ellipses (…) indicate existing text remains unchanged

### ITEM 1
CHAPTER 3 GENERAL REGULATIONS, SECTION 320.4

OSHPD proposes to amend sections listed below.

| OSHPD 05/25 ITEM 1 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 1-1 | 320.4 Telephone and Technology Equipment Centers | Approve | Accept |  | Revise OSHPD banner adding 2 & 5 and add new referenced section number. |  |
| - 1-2 | 320.4.4 | Approve | Accept |  | Add text that the section does not apply to OSHPD 2 & 5. |  |

### ITEM 2
CHAPTER 3, SECTION 321 ESSENTIAL MECHANICAL PROVISIONS

OSHPD proposes to amend section as listed below.

| OSHPD 05/25 ITEM 2 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 2-1 | 321.3 | Approve | Accept |  | Add text that the section does not apply to OSHPD 3 |  |

### ITEM 3
CHAPTER 4 VENTILATION AIR, SECTIONS 401.0, 402.0, 403.0 AND 407.0

OSHPD proposes to amend and/or add new sections listed below.

| OSHPD 05/25 ITEM 3 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 3-1 | 401.1 Applicability | Approve | Accept |  | Relocate OSHPD banner and text to the end of paragraph. |  |
| - 3-2 | 402.1 Occupiable Spaces | Approve | Accept |  | Repeal OSHPD paragraph and blend into section 402.1.2 to remove duplicative and repetitive language. |  |
| - 3-3 | 402.1.2 Ventilation in Health Care Facilities | Approve | Accept |  | Blend in the paragraph from 402.1 and add reference to section 403.0 for ventilation requirements. Add reference to the revised Table 4-C. |  |
| - 3-4 | 402.3 Mechanical Ventilation | Approve | Accept |  | Repeal OSHPD banner and text to allow pertinent information for mechanical ventilation to be used in this section. |  |
| - 3-5 | 402.4 Outdoor Air Intakes | Approve | Accept |  | Add new amendment for additional requirements for healthcare outside air intakes found in 407.2.1. |  |
| - 3-6 | 403.0 Ventilation Rates | Approve | Accept |  | Repeal OSHPD banner and text that did not permit the use for OSHPD 1, 2, 3, 4 & 5 spaces listed in Table 4-A |  |
| - 3-7 | 403.2 Zone Calculations | Approve | Accept |  | Add a reference to Table 4-A and section 407.3.1 for ventilation requirements. |  |
| - 3-8 | 407.3.1 | Approve | Accept |  | Add 3rd party for certified balancers. |  |
| - 3-9 | 407.3.1.1 Clinic Spaces | Approve | Accept |  | Add new section with requirements for ventilation systems to designed and balanced per Table 4-A or Table 4-C. |  |

### ITEM 4
CHAPTER 4, SECTIONS 408.0 and 415.0

OSHPD proposes to amend section as listed below.

| OSHPD 05/25 ITEM 4 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 4-1 | 408.2.1 | Approve | Accept |  | Add filtration level for spaces included in Table 4-A. |  |
| - 4-2 | 408.3.1 | Approve | Accept |  | Add filtration level for spaces included in Table 4-A. |  |
| - 4-3 | 408.4.1 | Approve | Accept |  | Add filtration level for spaces included in Tables 4-A or 4-C. |  |
| - 4-4 | 408.5.1 | Approve | Accept |  | Revise reference from Table 4-B to Table 4-A. |  |
| - 4-5 | 415.1 Air Distribution | Approve | Accept |  | Add HEPA filtration for terminal device. |  |

### ITEM 5
CHAPTER 4, TABLE 4-A

OSHPD proposes to amend Table 4-A as listed below.

| OSHPD 05/25 ITEM 5 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 5-1 | Table 4-A – Filtration Level | Approve | Accept |  | Add filtration level column. |  |
| - 5-2 | Table 4-A – Post-anesthesia care unit and recovery item | Approve | Accept |  | Replace ‘NR’ with “yes” in the column for Exhausted Directly to Outdoors. |  |
| - 5-3 | Table 4-A – Waiting area primary care clinic | Approve | Accept |  | Relocate this line item to Table 4-C. |  |
| - 5-4 | Table 4-A – Bronchoscopy, sputum collection, and pentamidine administration | Approve | Accept |  | Revise this to “Bronchoscopy” to align with national standard. |  |
| - 5-5 | Table 4-A – MRI room and Fluoroscopy room | Approve | Accept |  | Revise this line item for the Design Relative Humidity column from ‘NR’ to ‘MAX 60’ |  |
| - 5-6 | Table 4-A – Interventional imaging procedure room | Approve | Accept |  | Revise the required minimum outdoor air change rate from 5 ac/hr to 3 ac/hr |  |
| - 5-7 | Table 4-A - Dental treatment | Approve | Accept |  | Relocate this line item to Table 4-C |  |
| - 5-8 | Table 4-A – Drug room | Approve | Accept |  | Revise the space pressurization requirement to “positive” |  |
| - 5-9 | Table 4-A – Pharmacy compounding rooms (7 rooms) | Approve | Accept |  | Replace “NR” with footnote “dd” in the Minimum Outdoor Air Change Rate column. |  |
| - 5-10 | Table 4-A - Non-HD ante room | Approve | Accept |  | Revise air change rate from 30 ac/hr to 20 ac/hr |  |
| - 5-11 | Table 4-A – Warewashing | Approve | Accept |  | Repeal the footnote (r). |  |
| - 5-12 | Table 4-A – Sterilizing equipment room | Approve | Accept |  | Revise the recirculated room unit requirement from “No” to “NR”. |  |
| - 5-13 | Table 4-A – BEHAVIORAL HEALTH | Approve | Accept |  | Add 3 space functions to be listed under new section for Behavioral Health. Post CAC: HCAI added underline to temperature values |  |
| - 5-14 | Table 4-A – Skilled Nursing and Intermediate Care Facilities: AII room & AII anteroom | Approve | Accept |  | Revise footnote ‘b’ to footnote ‘u’. |  |
| - 5-15 | Table 4-A – Resident Corridor (1225.5.1.1) | Approve | Accept |  | Revise referenced section number to 1225.5.1.1. |  |
| - 5-16 | Table 4-A – Footnote b | Approve | Disagree |  | Revise referenced section to Board of Pharmacy requirements found in Title 16. Post CAC: HCAI corrected Title 16 Section numbers. |  |
| - 5-17 | Table 4-A – Footnote r | Approve | Accept |  | Replace model language with text regarding the newly added filtration level and direct code user to Table 4-B. |  |
| - 5-18 | Table 4-A – Footnote dd | Approve | Accept |  | Revise footnote to direct code user to Section 403 to calculate the required outside air change rate. |  |

### ITEM 6
CHAPTER 4, TABLE 4-B

OSHPD proposes to amend Table 4-B as listed below.

| OSHPD 05/25 ITEM 6 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 6-1 | Table 4-B | Approve | Accept |  | Consolidate Table 4-B to include requirements of Table 4-B and 4-C with further amendments. Amend the title of the table to include skilled nursing facilities, intermediate care facilities, and correction treatment centers adding OSHPD 2 & 4 to the banner. |  |
| - 6-2 | Table 4-B – Filtration Level | Approve | Accept |  | Add new column for ‘Filtration Level’. |  |

### ITEM 7
CHAPTER 4, TABLE 4-C

OSHPD proposes to amend Table 4-C as listed below.

| OSHPD 05/25 ITEM 7 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 7-1 | Table 4-C FILTER EFFICIENCIES FOR CENTRAL VENTILATION … [OSHPD 2 & 4] | Approve | Accept |  | Repeal Table 4-C about filter efficiencies and relocate the requirements of Table 4-C to Table 4-B. |  |
| - 7-2 | Table 4-C PRESSURE RELATIONSHIP & VENTILATION REQUIREMENTS FOR LICENSED CLINICS [OSHPD 3] | Approve | Accept |  | Add new Table 4-C related to ventilation requirements for certain licensed clinics. This table is based on Table 8-2 from the 2021 ASHRAE 170 Standard with further OSHPD amendments. |  |
| - 7-3 | Table 4-C Footnote a | Approve | Accept |  | Revise footnote a to reference appropriate California Mechanical Code (CMC) Section 407.4.5 |  |
| - 7-4 | Table 4-C Footnote b | Approve | Accept |  | Revise footnote b to clarify functions not specifically addressed in Table 8-2. |  |
| - 7-5 | Table 4-C Footnote c | Approve | Accept |  | Revise footnote c to refer to Table 4-B. |  |
| - 7-6 | Table 4-C Footnote d | Approve | Accept |  | Revise footnote d to match amendment in Table 4-A |  |
| - 7-7 | Table 4-C Footnote f | Approve | Accept |  | Revise references for the Facility Guidelines Institute to the appropriate California Building Code (CBC) Section. |  |
| - 7-8 | Table 4-C Footnote g | Approve | Accept |  | Revise to match the primary care clinic waiting room function of space. Note clarifies the room function is intended for primary care clinics and other clinic types. |  |
| - 7-9 | Table 4-C Footnote j | Approve | Accept |  | Replace model language with amended language from Table 4-A related to exhaust. |  |
| - 7-10 | Table 4-C Footnotes l & m & p | Approve | Accept |  | Revise references from Tables 7-1 / 8-1 to Table 4-A. |  |
| - 7-11 | Table 4-C Footnotes n & o | Approve | Accept |  | Revise references from Table 8-1 to Table 4-A and modify to match the CBC Section 1224. |  |
| - 7-12 | Table 4-C Footnote q | Approve | Accept |  | Replace model language with requirements of Section 403 for ventilation systems using air class design option. |  |
| - 7-13 | Table 4-C Footnote r | Approve | Accept |  | Add new footnote for toilet exhaust requirements. |  |

### ITEM 8
CHAPTER 5 EXHAUST SYSTEMS, SECTION 505.0 PRODUCT-CONVEYING SYSTEMS

OSHPD proposes to amend sections listed below.

| OSHPD 05/25 ITEM 8 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 8-1 | 507.7 505.13 Pharmaceutical Hazardous Drug (HD) Compounding Exhaust Discharge | Approve | Accept |  | Relocate this section and add ‘hazardous drug’ to identify that the requirements apply to hazardous exhaust. Revise discharge height from 7 to 10 feet to align with Section 407.2.2.1. |  |

### ITEM 9
CHAPTER 6 DUCT SYSTEMS, SECTION 602.0 MATERIAL

OSHPD proposes to amend section listed below.

| OSHPD 05/25 ITEM 9 | Code Section | CAC Action | Agency Response | Public Comments | Annotations | CBSC Action |
| --- | --- | --- | --- | --- | --- | --- |
| - 9-1 | 602.1 General | Approve | Disagree |  | Relocate OSHPD banner to the end of the exception and remove banner [Not permitted for OSHPD 1, 1R, 2, 3, 4 & 5] which is no longer needed. Post CAC: HCAI revised referenced section from 407.4.2 to 407.4.3. |  |