# CALIFORNIA BUILDING STANDARDS COMMISSION
September 1, 2026
CALGREEN EV WORKSHOP #1

Agenda Item 2c-2d
DRAFT EXPRESS TERMS
CALIFORNIA GREEN BUILDING STANDARDS CODE,
(CALGreen), PART 11,
CALIFORNIA BUILDING STANDARDS CODE,
TITLE 24, CALIFORNIA CODE OF REGULATIONS

If using assistive technology, please adjust your settings to recognize underline, strikeout and ellipsis.

## LEGEND for EXPRESS TERMS

- Existing California language appears upright.

- Proposed amendments appear in underline and strikeout.

- Ellipses (...) indicate existing text remains unchanged.

- Rationale: The justification for the change is shown after each section or series of related changes.

## AGENDA ITEM 2c
Reorganization of EV regulations

CHAPTER 5 NONRESIDENTIAL MANDATORY MEASURES

DIVISION 5.1 – PLANNING AND DESIGN

SECTION 5.106 – SITE DEVELOPMENT

…

5.106.5 Electric vehicle (EV) charging for new construction. [BSC-CG]

5.106.5.3  Electric vehicle (EV) charging. [BSC-CG] Newly constructed nonresidential buildings shall be provided with electric vehicle infrastructure to facilitate electric vehicle charging in accordance with Sections 5.106.5.3.1 and 5.106.5.3.2 and associated Table 5.106.5.3.1, or independently, Section 5.106.5.3.6 and associated Table 5.106.5.3.6. Electric vehicle supply equipment (EVSE) shall comply with the California Electrical Code.

New construction shall comply with Section 5.106.5.1 or Section 5.106.5.2. Electric vehicle supply equipment (EVSE) shall comply with the California Electrical Code.
 	Exceptions:

1. On a case…

2. Areas of parking…

5.106.5.1 Reserved Prescriptive method. When parking is provided, EV capable spaces and EVCS shall be provided in accordance with Table 5.106.5.1 and the following requirements:

1. EV capable spaces shall comply with Section 5.106.5.3 and EVCS shall comply with Section 5.106.5.4.

2. The EVCS shall be provided with Level 2 charger or DCFC.

3. [The following is moved from existing Table 106.5.3.1 footnote 1] 
Calculation for spaces shall be rounded up to the nearest whole number.

4. [The following is moved from existing Table 106.5.3.1 footnote 3 and amended] 
At least one Level 2 charger shall be provided when EVCS is required.

5.5.106.5.3.2.3 The installation of each DCFC EVSE shall be permitted to reduce the minimum number of required EV capable spaces without EVSE or separately EVCS with Level 2 charger EVSE by five, and reduce proportionally the required electrical load capacity to the service panel or subpanel.

6. 5.106.5.3.2.4 The installation of two low power Level 2 EV charging receptacles shall be permitted to reduce the minimum number of required EV capable spaces without EVSE in Table 5.106.5.3.1 by one. 5.106.5.3.2.4.1 Raceway capacity requirements. To allow for future upgrades to the electrical conductors serving low power Level 2 charging receptacles, the listed raceway serving such receptacles shall be sized to allow the installation of a dedicated 208/240-volt 40-ampere branch circuit. Where no raceway is used, the conductors shall be sized to accommodate a 208/240-volt 40-ampere receptacle.

TABLE 5.106.5.3 .1—EV CAPABLE SPACES AND EVCS

[New table added]

| TOTAL NUMBER OF ACTUAL PARKING SPACES | NUMBER OF REQUIRED EV CAPABLE SPACES | NUMBER OF REQUIRED EV CHARGING STATIONS (EVCS) |
| --- | --- | --- |
| Office and Retail |  |  |
| 1-9 | 0 | 0 |
| 10-25 | 1 | 3 |
| 26-50 | 2 | 6 |
| 51-75 | 4 | 9 |
| 76-100 | 5 | 12 |
| 101-150 | 6 | 19 |
| 151-200 | 9 | 26 |
| 201 & over | 5 percent of actual parking spaces | 15 percent of actual parking spaces |
| Other than Office and Retail |  |  |
| 1-9 | 0 | 0 |
| 10-25 | 2 | 2 |
| 26-50 | 4 | 4 |
| 51-75 | 7 | 6 |
| 76-100 | 9 | 8 |
| 101-150 | 13 | 12 |
| 151-200 | 17 | 18 |
| 201 & over | 10 percent of actual parking spaces | 10 percent of actual parking spaces |

| TOTAL NUMBER OF ACTUAL PARKING SPACES | NUMBER OF REQUIRED EV CAPABLE SPACES | Other than Office and Retail NUMBER OF REQUIRED EVCS 2, 3 | Office and Retail NUMBER OF REQUIRED EVCS 2, 3 |
| --- | --- | --- | --- |
| 1-9 | 0 | 0 | 0 |
| 10-25 | 4 | 2 | 3 |
| 26-50 | 8 | 4 | 6 |
| 51-75 | 13 | 6 | 8 |
| 76-100 | 17 | 8 | 13 |
| 101-150 | 25 | 12 | 19 |
| 151-200 | 35 | 18 | 26 |
| 201 and over | 20 percent of actual parking spaces 1 | 50 percent of EV capable spaces 1 | 75 percent of EV capable spaces 1 |

1. [The footnote is moved to Section 5.106.5.1] 
Calculation for spaces shall be rounded up to the nearest whole number.

2. Each EVCS shall reduce the number of required EV capable spaces by the same number.

3. [The footnote is moved to Section 5.106.5.1 and amended] 
At least one Level 2 EVSE shall be provided.

5.106.5.3.6 Electric vehicle charging stations (EVCS)—power allocation method. The power allocation method may be used as an alternative to the requirements in Section 5.106.5.3.1., Section 5.106.5.3.2 and associated Table 5.106.5.3.1. 
[The following is moved to Section 5.106.5.2 with some modifications] 
Use Table 5.106.5.3.6 to determine the total power in kVA required based on the total number of actual parking spaces.

Power allocation method shall include the following:

1. Use any kVA combination of EV capable spaces, low power Level 2, Level 2 or DCFC EVSEs complying with the following.

5.106.5.2 Reserved Power allocation method. When parking is provided, EV capable spaces and EVCS shall be provided with any kVA combination of EV capable spaces, low power Level 2, Level 2 or DCFC chargers in accordance with Table 5.106.5.2 and the following requirements:

1. [The following is moved from existing Section 5.106.5.3.6 and renumbered] 
Use Table 5.106.5.3.6 5.106.5.2 to determine the total power in kVA required based on the total number of actual parking spaces.

2. EV capable spaces shall comply with Section 5.106.5.3 and EVCS shall comply with Section 5.106.5.4.

3. Each EVCS shall be calculated for a minimum Level 2 EVSE.

4. [The following is moved from existing Table 106.5.3.6 footnote 2 and amended] 
At least one Level 2 EVSE shall be provided when EVCS is required.

5. [The following is moved from existing Table 106.5.3.6 footnote 5 with changes] 
Office and Retail: EV capable spaces shall utilize not more than 25 percent of total required kVA.

6. [The following is moved from existing Table 106.5.3.6 footnote 3 with changes] 
Other than Office and Retail: EV capable spaces shall utilize not more than 50 percent of total required kVA.

7. EV Capable spaces shall be calculated using a factor of 6.6 kVA per space.

TABLE 5.106.5.3.6  5.106.5.2 EVCS EV CHARGING– 
POWER ALLOCATION METHOD

| TOTAL NUMBER OF ACTUAL PARKING SPACES | MINIMUM TOTAL REQUIRED kVA @ 6.6 kVA | Other than Office and Retail TOTAL kVA REQUIRED IN ANY COMBINATION OF EV CAPABLE 3, 4, LOW POWER LEVEL 2, LEVEL 2 1, 2, OR DCFC | Office and Retail TOTAL kVA REQUIRED IN ANY COMBINATION OF EV CAPABLE 4, 5, LOW POWER LEVEL 2, LEVEL 2 1, 2, OR DCFC |
| --- | --- | --- | --- |
| 1-9 | 0 | 0 | 0 |
| 10-25 | 26.4 | 26.4 | 26.4 |
| 26-50 | 52.8 | 52.8 | 52.8 |
| 51-75 | 85.8 | 85.8 | 85.8 |
| 76-100 | 112.2 | 112.2 | 112.2 |
| 101-150 | 165 | 165 | 165 |
| 151-200 | 231 | 231 | 231 |
| 201 and over | 20 percent of actual parking spaces x 6.6 | Total required kVA =P x .20 x 6.6 Where P=Parking spaces in facility | Total required kVA =P x .20 x 6.6 Where P=Parking spaces in facility |

[The footnotes are moved to Section 5.106.5.2 with changes. Repeal footnotes 1 & 4]

1. Level 2 EVSE @ 6.6 kVA minimum.

2. At least one Level 2 EVSE shall be provided.

3. Maximum allowed kVA to be utilized for EV capable spaces is 75 percent.

4. If EV capable spaces are utilized, they shall meet the requirements of Section 5.106.5.3.1 EV capable spaces.

5. For office and retail buildings the maximum allowed kVA to be utilized for EV capable spaces is 25 percent.

[Renumbered Section 5.106.5.3. is relocated below new Section 5.106.5.2]

5.106.5.3.1.3 EV capable spaces. [N] When EV capable spaces are provided, they shall be provided in accordance with Table 5.106.5.3.1 and comply with the following requirements:

1.	Raceways complying with the California Electrical Code and no less than 1-inch (25 mm) diameter shall be provided and shall originate at a service panel or a subpanel(s) serving the area, and shall terminate in close proximity to the proposed location of the EV capable space and into a suitable listed cabinet, box, enclosure or equivalent. A common raceway may be used to serve multiple EV capable spaces. 
For each EV Capable Space, install a listed raceway to accommodate a dedicated 208/240-volt branch circuit. The raceway shall be not less than 1-inch (25 mm) inside diameter and shall originate at a service panel or a subpanel(s) serving the area. The raceway shall terminate in close proximity to the proposed location of the EV capable space into a suitable listed cabinet, box, or other enclosure. A common raceway may be used to serve multiple EV capable spaces. A raceway is not required if a minimum 40-ampere 208/240-volt dedicated EV branch circuit is installed in close proximity to the proposed location of an EV capable space at the time of original construction.

2.	A service panel or subpanel(s) shall be provided with panel space and electrical load capacity for a dedicated 208/240 volt, 40-ampere minimum branch circuit for each EV capable space, with delivery of 30-ampere minimum to an installed EVSE at each EVCS. 
The electrical service panel or subpanel(s) shall have the capacity for a 40-ampere 208/240-volt minimum dedicated branch circuit and space(s) reserved to permit installation of a branch circuit overcurrent protective device.

3.	The electrical system and any on-site distribution transformers shall have sufficient capacity to supply full rated amperage at each EV capable space.

4.	The service panel or subpanel circuit directory shall identify the reserved overcurrent protective device space(s) as “EV CAPABLE”. The raceway termination location shall be permanently and visibly marked as “EV CAPABLE.”

Note: A parking space served by electric vehicle supply equipment or designed as a future EV charging space shall count as at least one standard automobile parking space only for the purpose of complying with any applicable minimum parking space requirements established by an enforcement agency. See Vehicle Code Section 22511.2 for further details.

5.106.5.3.2.4 Electric vehicle charging stations (EVCS). When EVCS are provided, they shall comply with the following requirements:

1. EV capable spaces shall be provided with electric vehicle supply equipment (EVSE) to create EVCS in the number indicated in Table 5.106.5.3.1. The EVCS required by Table 5.106.5.3.1 shall be provided with Level 2 EVSE or DCFC as permitted in Section 5.106.5.3.2.3. At least one Level 2 EVSE shall be provided.

2. Multiple connectors. One EV charger with multiple connectors capable of charging multiple EVs simultaneously shall be permitted if the electrical load capacity required by Section 5.106.5.3.1 for each EV capable space is accumulatively supplied to the EV charger.

3. 5.106.5.3.2.2 EV charger connectors. EV chargers shall be equipped with SAE J1772 connectors with a maximum output of 240 Volts AC or SAE J3400 connectors. When using level 2 SAE J3400 SAE connectors, supplied by a 480 V 3-phase service, at least 20 percent of the EV charger connectors shall be SAE J1772 connectors with a maximum output of 240 Volts AC.

4. 5.106.5.3.2.1 Receptacle configurations. 208/240V EV charging receptacles shall comply with one of the following configurations:

  - For 20-ampere receptacles, NEMA 6-20R

  - For 30-ampere receptacles, NEMA 14-30R

  - For 50-ampere receptacles, NEMA 14-50R

5. 5.106.5.3.4  Accessible electric vehicle charging station (EVCS). ...

6. 5.106.5.3.5  Electric vehicle charging station signage. …

[Section 5.106.5.3.2.4.1 Raceway capacity requirements is relocated to Section new Section 5.106.5.1 item 6].

5.106.5.3.3 5.106.5.5 Use of automatic load management systems (ALMS). ALMS shall be permitted for EVCS. When ALMS is installed, the required electrical load capacity specified in Section 5.106.5.3.1 4 for each EVCS may be reduced when serviced by an EVSE controlled by an ALMS. Each EVSE controlled by an ALMS shall deliver a minimum 6.2kW to an EV when charging one vehicle and shall deliver a minimum 3.3 kW while simultaneously charging multiple EVs.

REVISED LANGUAGE IF APPROVED (CLEAN VERSION)

5.106.5 Electric vehicle (EV) charging for new construction. [BSC-CG]

New construction shall comply with Section 5.106.5.1 or Section 5.106.5.2. Electric vehicle supply equipment (EVSE) shall comply with the California Electrical Code.
 	Exceptions:

1. On a case…

2. Areas of parking…

5.106.5.1 Prescriptive method. When parking is provided, EV capable spaces and EVCS shall be provided in accordance with Table 5.106.5.1 and the following requirements:

1. EV capable spaces shall comply with Section 5.106.5.3 and EVCS shall comply with Section 5.106.5.4.

2. The EVCS shall be provided with Level 2 charger or DCFC.

3. Calculation for spaces shall be rounded up to the nearest whole number.

4. At least one Level 2 charger shall be provided when EVCS is required.

5.The installation of each DCFC shall be permitted to reduce the minimum number of required EV capable spaces or separately EVCS with Level 2 charger by five, and reduce proportionally the required electrical load capacity to the service panel or subpanel.

6.The installation of two low power Level 2 EV charging receptacles shall be permitted to reduce the minimum number of required EV capable spaces by one. To allow for future upgrades to the electrical conductors serving low power Level 2 charging receptacles, the listed raceway serving such receptacles shall be sized to allow the installation of a dedicated 208/240-volt 40-ampere branch circuit. Where no raceway is used, the conductors shall be sized to accommodate a 208/240-volt 40-ampere receptacle.

TABLE 5.106.5.1—EV CAPABLE SPACES AND EVCS

| TOTAL NUMBER OF ACTUAL PARKING SPACES | NUMBER OF REQUIRED EV CAPABLE SPACES | NUMBER OF REQUIRED EV CHARGING STATIONS (EVCS) |
| --- | --- | --- |
| Office and Retail |  |  |
| 1-9 | 0 | 0 |
| 10-25 | 1 | 3 |
| 26-50 | 2 | 6 |
| 51-75 | 4 | 9 |
| 76-100 | 5 | 12 |
| 101-150 | 6 | 19 |
| 151-200 | 9 | 26 |
| 201 & over | 5 percent of actual parking spaces | 15 percent of actual parking spaces |
| Other than Office and Retail |  |  |
| 1-9 | 0 | 0 |
| 10-25 | 2 | 2 |
| 26-50 | 4 | 4 |
| 51-75 | 7 | 6 |
| 76-100 | 9 | 8 |
| 101-150 | 13 | 12 |
| 151-200 | 17 | 18 |
| 201 & over | 10 percent of actual parking spaces | 10 percent of actual parking spaces |

5.106.5.2 Power allocation method. When parking is provided, EV capable spaces and EVCS shall be provided in any kVA combination of EV capable spaces, low power Level 2, Level 2 or DCFC chargers in accordance with Table 5.106.5.2 and the following requirements:

1. Use Table 5.106.5.2 to determine the total power in kVA required based on the total number of actual parking spaces.

2. EV capable spaces shall comply with Section 5.106.5.3 and EVCS shall comply with Section 5.106.5.4.

3. Each EVCS shall be calculated for a minimum Level 2 EVSE

4. At least one Level 2 EVSE shall be provided when EVCS is required.

5. Office and Retail: EV capable spaces shall utilize not more than 25 percent of total required kVA.

6. Other than Office and Retail: EV capable spaces shall utilize not more than 50 percent of total required kVA.

7. EV Capable spaces shall be calculated using a factor of 6.6 kVA per space.

TABLE 5.106.5.2 EV CHARGING– 
POWER ALLOCATION METHOD

| TOTAL NUMBER OF ACTUAL PARKING SPACES | TOTAL REQUIRED kVA |
| --- | --- |
| 1-9 | 0 |
| 10-25 | 26.4 |
| 26-50 | 52.8 |
| 51-75 | 85.8 |
| 76-100 | 112.2 |
| 101-150 | 165 |
| 151-200 | 231 |
| 201 and over | 20 percent of actual parking spaces x 6.6 |

5.106.5.3 EV capable spaces. When EV capable spaces are provided, they shall comply with the following requirements:

1.	For each EV Capable Space, install a listed raceway to accommodate a dedicated 208/240-volt branch circuit. The raceway shall be not less than 1-inch (25 mm) inside diameter and shall originate at a service panel or a subpanel(s) serving the area. The raceway shall terminate in close proximity to the proposed location of the EV capable space into a suitable listed cabinet, box, or other enclosure. A common raceway may be used to serve multiple EV capable spaces. A raceway is not required if a minimum 40-ampere 208/240-volt dedicated EV branch circuit is installed in close proximity to the proposed location of an EV capable space at the time of original construction.

2.	The electrical service panel or subpanel(s) shall have the capacity for a 40-ampere 208/240-volt minimum dedicated branch circuit and space(s) reserved to permit installation of a branch circuit overcurrent protective device.

3.	The electrical system and any on-site distribution transformers shall have sufficient capacity to supply full rated amperage at each EV capable space.

4.	The service panel or subpanel circuit directory shall identify the reserved overcurrent protective device space(s) as “EV CAPABLE”. The raceway termination location shall be permanently and visibly marked as “EV CAPABLE.”

Note: A parking space served by electric vehicle supply equipment or designed as a future EV charging space shall count as at least one standard automobile parking space only for the purpose of complying with any applicable minimum parking space requirements established by an enforcement agency. See Vehicle Code Section 22511.2 for further details.

5.106.5.4 Electric vehicle charging stations (EVCS). When EVCS are provided, they shall comply with the following requirements:

1. EV capable spaces shall be provided with electric vehicle supply equipment (EVSE) to create EVCS.

2. Multiple connectors. One EV charger with multiple connectors capable of charging multiple EVs simultaneously shall be permitted if the electrical load capacity required by Section 5.106.5.3.3 for each EV capable space is accumulatively supplied to the EV charger.

3. EV charger connectors. EV chargers shall be equipped with SAE J1772 with a maximum output 240 Volts AC or SAE J3400 connectors. When using level 2 SAE J3400 SAE connectors, supplied by a 480 V 3-phase service, at least 20 percent of the EV charger connectors shall be SAE J1772 with a maximum output 240 Volts AC.

4. Receptacle configurations. 208/240V EV charging receptacles shall comply with one of the following configurations:

- For 20-ampere receptacles, NEMA 6-20R

- For 30-ampere receptacles, NEMA 14-30R

- For 50-ampere receptacles, NEMA 14-50R

5. Accessible electric vehicle charging station (EVCS). ...

6. Electric vehicle charging station signage. …

5.106.5.5 Use of automatic load management systems (ALMS). ALMS shall be permitted for EVCS. When ALMS is installed, the required electrical load capacity specified in Section 5.106.5.4 for each EVCS may be reduced when serviced by an EVSE controlled by an ALMS. Each EVSE controlled by an ALMS shall deliver a minimum 6.2kW to an EV when charging one vehicle and shall deliver a minimum 3.3 kW while simultaneously charging multiple EVs.

RATIONALE:

BSC-CG is proposing to amend Electric vehicle code Sections 5.106.5.3 and various subsections to simplify the application of the EV regulations. The changes are mainly to reformatting the existing EV capable table to clearly illustrate the required number of EV capable spaces based on the actual parking spaces for the two occupancy types (office and retail and other than office & retail. 
For the power allocation method table BSC simplified by removing two columns.  While the format and the percentages changed there is no real change in regulatory effect as the numbers were mostly maintained with few numbers that were adjusted for accuracy.

Additionally, some related EV sub sections were relocated below the applicable tables and editorial corrections and added titles were made to code sections as needed.

### AGENDA ITEM 2d
Additions and alterations

5.106.5.4 6 Additions or alterations to existing buildings or parking facilities. [BSC-CG] Existing buildings or parking facilities being modified in accordance with one of the following, shall comply with Section 5.106.5.4.1 or 5.106.5.4.2.

1. When the scope of construction work includes an increase in power supply to an electric service panel as part of a parking facility addition or alteration.

2. When a new photovoltaic system is installed covering existing parking spaces. 
Only parking spaces physically covered by the new photovoltaic system panels shall count toward the EV charging requirements.

3. When additions or alterations to existing buildings are triggered pursuant to code Section 301.3 and the scope of work includes an increase in power supply to an electric service panel.

Additions or alterations to existing buildings or parking facilities shall comply with Sections 5.106.5.6.1 or 5.106.5.6.2 when the scope of work includes any of the following:

  - Increase in power supply to an electric service panel as part of a parking facility addition or alteration.

  - Installation of a new photovoltaic system covering existing parking spaces. 
Only parking spaces physically covered by the new photovoltaic system panels shall count toward the total number of actual parking spaces applicable to the EV charging requirements.

  - Additions or alterations to existing buildings that are required to comply with CALGreen pursuant to Section 301.3 and require an increase in the required number of parking spaces. 
Only newly added parking spaces shall count toward the EV charging requirements.

5.106.5.4 6.1 Existing buildings or parking areas without previously installed EV capable infrastructure. …

5.106.5.4 6.2 Existing buildings or parking areas with previously installed EV capable infrastructure. …

5.106.5.4 6.3 Accessible electric vehicle charging station (EVCS). 
When EVSE is installed, accessible EVCS shall be provided in accordance with the California Building Code, Chapter 11B, Section 11B-228.3.

#### RATIONALE:

BSC-CG is proposing to amend renumbered Section 5.106.5.6 main paragraph and triggers 1, 2 and 3 for additions or alterations to existing buildings or parking facilities. The main paragraph is amended to renumber from 5.106.5.4 to 5.106.5.6 and amend the charging language to simply reference the three revised triggers.

Trigger 1:
The purpose for the proposed code change to trigger 1 is to clarify the intent by rewording the scoping requirements for when there is an increase in power supply to an electric service panel as part of a parking facility addition or alteration. This proposed change does not have a regulatory effect.

Trigger 2:
The purpose for the proposed code change to trigger 2 is to clarify the intent by rewording the scoping requirements for when new photovoltaic system projects cover existing parking spaces. Existing spaces not covered by the new photovoltaic system project do not count toward the requirement for EV charging. This proposed change does not have a regulatory effect.

Trigger 3:	
The proposed change to trigger 3 is to clarify the intent by rewarding the scoping requirements.

The specific change replaces references to increasing power supply for an electric service panel with new code language stating that this section applies when the required number of parking spaces increases instead.

Additionally, like trigger 2, new language is added to specify that only the newly added parking spaces shall count toward the number of actual parking spaces used for the EV charging requirements. Existing parking spaces do not count toward the requirement for EV charging. This proposed change may have a regulatory effect.

5.106.5.5 7 Medium-duty and heavy-duty…

5.106.5.6 8 Electric vehicle (EV) charging at Public schools and community colleges. [DSA-SS]

…

5.106 .8 9 Light pollution reduction….