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DRAFT EXPRESS TERMS 
AGENDA ITEM 3l
CHAPTER 5 NONRESIDENTIAL MANDATORY MEASURES,
DIVISION 5.5 – ENVIRONMENTAL QUALITY
SECTION 5.506 INDOOR AIR QUALITY
5.506.3 Carbon dioxide (CO2) monitoring in classrooms.
[DSA-SS] …
[BSC-CG] …
[DSA-SS, BSC-CG] The carbon dioxide monitor or sensor shall meet the following requirements:
1. The monitor or sensor shall continuously display the carbon dioxide reading and be permanently affixed in a tamper-proof manner in each classroom between 3 and 6 feet (914 mm and 1829 mm) above the floor and at least 5 feet (1524 mm) away from doors and operable windows.
2.  When the monitor or sensor is not integral to an Energy Management Control System (EMCS), the monitor or sensor shall display the carbon dioxide readings on the device. When the sensor is integral to an EMCS, or the carbon dioxide readings shall be available to and regularly monitored by facility personnel.
32. A The monitor or sensor shall provide notification through a visual indicator on the monitor in the space it serves when the carbon dioxide levels in the classroom exceed 1,100 ppm and. A sensor integral to an EMCS shall provide notification to facility personnel through a visual and/or audible indicator when the carbon dioxide levels in the classroom exceed 1,100 ppm.
4. The monitor or EMCS devices used to measure carbon dioxide levels shall maintain a record of previous data that includes at least the maximum carbon dioxide concentration measured.
5 The monitor or sensor used to measure carbon dioxide levels shall have the capacity to measure carbon dioxide levels with a range of 400 ppm to 2000 ppm or greater.
6. The monitor or sensor shall be certified by the manufacturer to be accurate within 75 ppm at 1,000 ppm carbon dioxide concentration and shall be certified by the manufacturer to require calibration no more frequently than once every 5 years.
3. The monitor or sensor shall be certified by the manufacturer to be accurate within 75 ppm at 1,000 ppm, require calibration no more frequently than once every five years, and have the capacity to measure carbon dioxide levels with a range of 400 ppm to 2000 ppm or greater.
…
RATIONALE: 
BSC is proposing to revise Section 5.506.3 to clarify CO2 monitoring requirements in coordination with DSA. Current CO2 monitoring requirements have been difficult for code users to meet as only a few manufacturers are making products capable of meeting them. BSC and DSA propose these changes to simplify the requirements, make them more achievable, better match with similar code language in the California Energy Code, and realign with the original intent of this code section and CalSHAPE.
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