DIVISION OF THE STATE ARCHITECT

2018	TRIENNIAL CODE CYCLE

GREEN BUILDING FOCUS GROUP

WORKSHOP #1

October 10, 2017 – Agenda Item 2

Electric Vehicles’ Infrastructure

DRAFT EXPRESS TERMS for the 2018

CALIFORNIA GREEN BUILDING STANDARDS CODE

(CALGreen Code) PART 11

TITLE 24, CALIFORNIA CODE OF REGULATIONS

Proposed code language for the 2018 Intervening Code Cycle

LEGEND FOR DRAFT EXPRESS TERMS - Existing California amendments or code language being modified are in italics when they appear in the model code text: All such language appears in italics, modified language is underlined. - New California amendments: All such language appears underlined and in italics. - Repealed text: All such language appears in strikeout.

Electrical Vehicles

Section 5.106

SITE DEVELOPMENT

      - Electric vehicle (EV) charging. [N] Construction shall comply with Section 5.106.5.3.1 or Section 5.106.5.3.2 to facilitate future installation of electric vehicle supply equipment (EVSE). When EVSE(s) is/are installed, it shall be in accordance with the California Building Code, the California Electrical Code and as follows:

        - Single charging space requirements. [N]  When only a single charging space is required per Table 5.106.5.3.3, a raceway is required to be installed at the time of construction and shall be installed in accordance with the California Electrical Code. Construction plans and specifications shall include, but are not limited to, the following:

          - The type and location of the EVSE.

          - A listed raceway capable of accommodating a 208/240-volt dedicated branch circuit.

          - The raceway shall not be less than trade size 1”

4. The raceway shall originate at a service panel or a subpanel serving the area, and shall terminate in close proximity to the proposed location of the charging equipment and into a listed suitable cabinet, box, enclosure or equivalent.

5. The service panel or subpanel shall have sufficient capacity to accommodate a minimum 40-amprere dedicated branch circuit for the future installation of the EVSE.

        - Multiple charging space requirements. [N] When multiple charging spaces are required per Table 5.106.5.3.3 raceway(s) is/are required to be installed at the time of construction and shall be installed in accordance with the California Electrical Code. Construction plans and specifications shall include, but are not limited to, the following:

          - The type and location of the EVSE.

          - The raceway(s) shall originate at a service panel or a subpanel(s) serving the area, and shall terminate in close proximity to the proposed location of the charging equipment and into listed suitable cabinet(s), box(es), enclosure(s) or equivalent.

          - Plan design shall be based upon 40-amprere minimum branch circuits.

          - Electrical calculations shall substantiate the design of the electrical system, to include the rating of equipment and any on-site distribution transformers and have sufficient capacity to simultaneously charge all required EVs at its full rated amperage.

          - The service panel or subpanel(s) shall have sufficient capacity to accommodate the required number of dedicated branch circuit(s) for the future installation of the EVSE.

        - EV charging space calculation. [N] Table 5.106.5.3.3 shall be used to determine if single or multiple charging space requirements apply for the future installation of EVSE.

Exceptions: On a case-by-case basis where the local enforcing agency has determined EV charging and infrastructure is not feasible based upon one or more of the following conditions:

          - Where there is insufficient electrical supply.

          - Where there is evidence suitable to the local enforcing agency substantiating that additional local utility infrastructure design requirements, directly related to the implementation of Section 5.106.5.3, may adversely impact the construction cost of the project.

## Table 5.106.5.3.3

| Total number of parking spaces | Number of required EV charging spaces |
| --- | --- |
| 0-50 | 0 |
| 51-75 | 1 |
| 76-100 | 2 |
| 101-200 | 3 |
| 201 and over | 3% 1 |

            - Calculation for spaces shall be rounded up to the nearest whole number.

        - [N] Identification. The service panel or subpanel(s) circuit directory shall identify the reserved overcurrent protective device space(s) for future EV charging as “EV CAPABLE”. The raceway termination location shall be permanently and visibly marked as “EV CAPABLE.”

        - [N] Future charging spaces qualify as designated parking as described in Section 5.106.5.2 Designated parking.

## Notes:

- The California Department of Transportation adopts and publishes the California Manual on Uniform Traffic Control Devices (California MUTCD) to provide uniform standards and specifications for all official traffic control devices in California. Zero Emission Vehicle Signs and Pavement Markings can be found in the New Policies & Directives number 13-01. www.dot.ca.gov/hq/traffops/signtech/signdel/policy.htm

- See Vehicle Code Section 22511 for EV charging spaces signage in off-street parking facilities and for use of EV charging spaces.

- The Governor’s Office of Planning and Research published a Zero-Emission Vehicle Community Readiness Guidebook which provides helpful information for local governments, residents and businesses. http://opr.ca.gov/docs/ZEV_Guidebook.pdf